## SUMMARY (2)
INITIAL (AS FOUND) AIR BALANCE SCHEDULE
|  | HVAC SUPPLY |  | DEVIATION | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | PASS/FAIL | DESIGN | ACTUAL | 110%-90% | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FAIL | 1600 | 1234 | 77.12% | 1250 | 918 | 350 | 316 | 21.88% | 25.61%
RTU-2 | FAIL | 2400 | 1977 | 82.38% | 1900 | 1727 | 500 | 250 | 20.83% | 12.65%
RTU-3 | PASS | 2400 | 2343 | 97.62% | 1900 | 1837 | 500 | 506 | 20.83% | 21.6%
MUA-1 | FAIL |  |  | 67.33% | [6 empty] | 1200 | 808
KEF1 | [12 empty] | 700 | 700
KEF2 | [12 empty] | 803 | 803
KEF3 | [12 empty] | 718 | 718
EF1 | [14 empty] | 39 | 39
EF2 | [14 empty] | 57 | 57
TOTALS |  | 6400 | 5554 | 86.78% | 5050 | 4482 | 1350 | 1072 | 79.41% |  | 1200 | 808 | 2221 | 2221 | 96 | 96
NET BUILDING AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [8 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2550 | 1880 |  |  | FRONT |  | - | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2317 | 2317 |  |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 233 | -437 |  |  | REAR |  | - | [8 empty] | FALSE
[6 empty] | AVERAGE |  | -0.03 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT |  |  | FILTER TYPE/#/SIZE |  |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD |  |  | SOLO 9 16X16 |  |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250