## SUMMARY (2)
PENN STATION - FINAL (AFTER ADJUSTMENTS) AIR BALANCE SCHEDULE
|  | HVAC SUPPLY |  | DEVIATION | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | PASS / FAIL | DESIGN | ACTUAL | 110%-90% | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | PASS | 1600 | 1532 | 95.75% | 1250 | 1197 | 350 | 335 | 21.88% | 21.87%
RTU-2 | PASS | 2400 | 2511 | 104.6% | 1900 | 2043 | 500 | 468 | 20.83% | 18.64%
RTU-3 | PASS | 2400 | 2343 | 97.62% | 1900 | 1837 | 500 | 506 | 20.83% | 21.6%
MUA-1 | FAIL |  |  | 84.83% | [6 empty] | 1200 | 1018
KEF1 | [12 empty] | 700 | 700
KEF2 | [12 empty] | 803 | 803
KEF3 | [12 empty] | 718 | 718
EF1 | [14 empty] | 39 | 39
EF2 | [14 empty] | 57 | 57
TOTALS |  | 6400 | 6386 | 99.78% | 5050 | 5077 | 1350 | 1309 | 96.96% |  | 1200 | 1018 | 2221 | 2221 | 96 | 96
NET BUILDING AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [8 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2550 | 2327 |  |  | FRONT |  | - | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2317 | 2317 |  |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 233 | 10 |  |  | REAR |  | - | [8 empty] | FALSE
[6 empty] | AVERAGE |  | -0.03 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT |  |  | FILTER TYPE/#/SIZE |  |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD |  |  | SOLO 9 16X16 |  |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250