## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | BAR | 3900 | 2241 | 900 | -700 | 3000 | 2941 | 76.92% | 131.2%
AHU-2 | DINING | 3600 | 1943 | 715 | -824 | 2885 | 2767 | 80.14% | 142.4%
AHU-3 | KITCHEN | 4000 | 3982 | 3885 | 3858 | 115 | 124 | 2.875% | 3.114%
MUA-1 | HOODS | [8 empty] | 7400 | 7120
EF-1 | HOOD | [10 empty] | 1700 | 684
EF-2 | HOOD | [10 empty] | 2650 | 2520
EF-3 | HOOD | [10 empty] | 2650 | 2307
EF-4 | HOOD | [10 empty] | 1750 | 1742
EF-5 | DISHWASH | [12 empty] | 375 | 0
EF-6 | RESTROOMS | [12 empty] | 300 | 281
TOTALS |  | 11500 | 8166 | 5500 | 2334 | 6000 | 5832 |  |  | 7400 | 7120 | 8750 | 7253 | 675 | 281
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 13400 | 12952 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 9425 | 7534 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 3975 | 5418 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
AHU-1&2 HAVE MORE OUTSIDE AIR BEING DELIVERED TO THE OPEN RETURN THAN THEY CAN SUPPLY. THE RESULT IS THAT AIR FROM THE OAU THAT IS DELIVERED TO THESE AHUs IS SPILLING OUT INTO THE CEILING.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0