## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6000 | 6343 | 4955 | 5251 | 1045 | 1092 | 17.42% | 17.22%
RTU-2 | KITCHEN | 2000 | 1952 | 1566 | 1517 | 434 | 435 | 21.7% | 22.28%
MUA-1 | MUA | [8 empty] | 2821 | 2863
EF-1 | FRYERS | [10 empty] | 1662 | 1701
EF-2 | GRILL | [10 empty] | 1852 | 1848
EF-3 | TOILET/MOP SINK | [12 empty] | 375 | 357
EF-4 | CO2 ROOM | [12 empty] | 75 | 0
TOTALS |  | 8000 | 8295 | 6521 | 6768 | 1479 | 1527 |  |  | 2821 | 2863 | 3514 | 3549 | 375 | 357
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4300 | 4390 |  | FRONT |  | 0.0061 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3889 | 3906 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 411 | 484 |  | REAR |  | 0.0012 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00365 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0