## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FC-1 | DINING | 2235 | 2277 | 1755 | 1790 | 480 | 487 | 21.48% | 21.39%
FC-2 | BACK OF HOUSE | 1400 | 1365 | 1250 | 1220 | 150 | 145 | 10.71% | 10.62%
FC-3 | KITCHEN | 2235 | 2193 | 1985 | 1934 | 250 | 259 | 11.19% | 11.81%
MUA-1 | KITCHEN | [8 empty] | 2205 | 2194
KEF-1 | HOODS | [10 empty] | 2756 | 2760
EF-1 | RESTROOM | [12 empty] | 250 | 248
TOTALS |  | 5870 | 5835 | 4990 | 4944 | 880 | 891 |  |  | 2205 | 2194 | 2756 | 2760 | 250 | 248
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3085 | 3085 |  | FRONT |  | 0.0093 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3006 | 3008 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 79 | 77 |  | REAR |  | 0.0043 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0068 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2205
TOTAL KITCHEN EXHAUST |  | 3006
NET AIRFLOW |  | -801 | 0
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0