## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 3862 | 3500 | 3331 | 500 | 531 | 12.5% | 13.75%
RTU-2 | DINING | 5200 | 4753 | 4100 | 3562 | 1100 | 1191 | 21.15% | 25.06%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1897
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3288
EF-2 | RESTROOM | [12 empty] | 300 | 302
TOTALS |  | 9200 | 8615 | 7600 | 6893 | 1600 | 1722 |  |  | 1950 | 1897 | 3200 | 3288 | 300 | 302
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3550 | 3619 |  | FRONT |  | 0.0099 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3500 | 3590 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 29 |  | REAR |  | 0.0072 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00855 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250