## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BOH | 2100 | 2300 | 1715 | 1914 | 385 | 386 | 18.33% | 16.78%
RTU-2 | SALES | 5000 | 4292 | 3800 | 3430 | 1200 | 862 | 24% | 20.08%
RTU-3 | SALES | 4000 | 3852 | 3050 | 2855 | 950 | 997 | 23.75% | 25.88%
EF-1 | M. RR | [12 empty] | 70 | 56
EF-2 | W. RRW | [12 empty] | 70 | 58
EF-3 | PET AREAS | [12 empty] | 1220 | 1117
TOTALS |  | 11100 | 10444 | 8565 | 8199 | 2535 | 2245 |  |  | 0 | 0 | 0 | 0 | 1360 | 1231
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2535 | 2245 |  | FRONT |  | -0.02 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 1360 | 1231 |  | LOADING |  | -0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 1175 | 1014 |  | REAR |  | -0.01 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.013333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0