# Tesla Dublin 07/15/24

# Overview

- Balanced mezzanine office and conference room to design.

- Fully closed supply damper to restrooms but unable to get them down to 25 CFM.

- Increased airflow to entryway higher than design CFM, did not see a large change in space temp.

- Reduced OA from 950 CFM initial flow to 221 CFM.

- I suspect the space is struggling to cool based off ceiling height, and numerous glass windows that heat the space with sunlight.

- Observed temps near thermostat set point early in morning, but as the day progressed and temps rise, the space temp rises with it.

# Issues

- RTU-12 ductwork in mezzanine and shop is condensating due to temp differences in supply air inside duct and space temp.

- Return for mezzanine ductwork is taped off with cardboard restricting return flow.

- Ductwork in mezzanine level is not insulated, supply air temp is cooler than space temp (63 F / 75 F).

- Closing ductwork to mezzanine level will restrict airflow, and potentially raise temp, causing duct condensation to worsen.

- RTU-11 does not serve entry way. Shut of @ breaker and read entry way diffusers to verify.

- RTU-11 not operational on day of arrival, contacted Bridget @ Brinco. She put me in contact with Alex @ Air Fast. A technician arrived around noon on Tuesday and solved a wiring issue that made RTU-11 operational.

- RTU-12 economizer not functional, suspect an issue with modulator or controller. OA set manually.

- RTU-12 belt very loose causing below design CFM, tightened belt increasing fan RPM from 465 to 870.

- OA filter for RTU-12 was completely blocked with dust/debris upon arrival. I removed it from the unit and cleaned it out with a pressure washer. I suggest doing this periodically for all units.

# Temps and Conditions

Outside air conditions day 1: 87 F / 57% humidity

Outside air conditions day 2: 88 F / 51% humidity

Pressure of Entry Way: 0.0009”

Pressure of Shop: -0.0025”

Temp & Humidity of mezzanine area @ walking height: 75 F / 54.4%

Temp & Humidity of mezzanine area @ duct height: 75 F / 59.9%

Initial Interior Temp: 77 F

Initial Interior Temp Set Pt: 70 F

Post Interior Temp: 76 F

Post Interior Temp Set Pt: 67 F

# Entry Way Supply Air Temp, Humidity, & Flow Pre-Adjustments

- 67.9 F / 77.4 % / 184 CFM

- 69.2 F / 78.3 % / 207 CFM

- 70.5 F / 77.5 % / 225 CFM

- 69.3 F / 76.6 % / 178 CFM

- 69.5 F / 75.2 % / 191 CFM

# Entry Way Supply Air Temp, Humidity, & Flow Post-Adjustments

- 66.6 F / 75.4 % / 348 CFM

- 68.7 F / 70.3% / 362 CFM

- 67.9 F / 72.6 % / 384CFM

- 66.5 F / 69.8 % / 372 CFM

- 66.2 F / 70.9 % / 338 CFM

# Entry Way Return Air Temp, Humidity, & Flow Pre-Adjustments

- 76.8 F / 54.5 % / 183 CFM

- 77.1 F / 53.6 % / 284 CFM

# Entry Way Return Air Temp, Humidity, & Flow Post-Adjustments

- 75.4 F / 53.8 % / 456 CFM

- 75.9 F / 54.2 % / 552 CFM