## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 6000 | 5864 | 6000 | 5864 | 0 | 0 | 0% | 0%
RTU-2 |  | 6000 | 6088 | 6000 | 6088 | 0 | 0 | 0% | 0%
MUA-1 | [9 empty] | 5372 | 2576
KX-1 | [11 empty] | 3597 | 3498
KX-2 | [11 empty] | 3117 | 3287
DWX-1 | [11 empty] | 600 | 278
TX-1 | ROOF MNTD | [12 empty] | 375 | 0
TOTALS |  | 12000 | 11952 | 12000 | 11952 | 0 | 0 |  |  | 5372 | 2576 | 7314 | 7063 | 375 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5372 | 2576 |  | FRONT |  | -0.069 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 7689 | 7063 |  | SIDE |  | -0.075 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -2317 | -4487 |  | REAR |  | -0.079 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.074333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0