## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | SALES FLOOR | 25000 | 23350 | 25000 | 23350 | 0 | 0 | 0% | 0%
AC-2 | BAKERY | 1200 | 1274 | 1200 | 1274 | 0 | 0 | 0% | 0%
AC-3 | DELI | 1200 | 1254 | 1200 | 1254 | 0 | 0 | 0% | 0%
AC-4 | CONTROL ROOM | 1200 | 1258 | 1200 | 1258 | 0 | 0 | 0% | 0%
AC-5 | DRIVE N GO | 800 | 776 | 720 | 695 | 80 | 81 | 10% | 10.44%
DOAS-1 | SALES FLOOR | [8 empty] | 5500 | 5405
EF-1 | DELI HOOD | [10 empty] | 1800 | 1970
EF-2 | DISH WASHER | [10 empty] | 450 | 0
EF-3 | PAN WASHER | [10 empty] | 525 | 0
EF-4 | BAKERY HOOD | [10 empty] | 600 | 0
EF-5 | BAKERY OVENS | [12 empty] | 800 | 1223
EF-6 | BAKERY OVENS | [12 empty] | 800 | 1050
EF-7 | RESTROOM | [12 empty] | 100 | 0
EF-8 | JANITOR ROOM | [12 empty] | 150 | 0
EF-9 | MEAT CUT + WRAP | [12 empty] | 450 | 0
EF-10 | FLOWER STORAGE | [12 empty] | 100 | 93
EF-11 | RESTROOMS | [12 empty] | 280 | 282
EF-12 | BAKERY | [12 empty] | 4500 | 0
TOTALS |  | 29400 | 27912 | 29320 | 27831 | 80 | 81 |  |  | 5500 | 5405 | 3375 | 1970 | 7180 | 2648
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 5580 | 5486 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 10555 | 4618 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | -4975 | 868 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
Unable to test building pressure. Open grocery store with automatic sliding doors.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0