## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BAR/BAR DINING | 4400 | 4441 | 3350 | 3341 | 1050 | 1100 | 23.86% | 24.77%
RTU-2 | WAITING & DINING | 4400 | 4593 | 3350 | 3583 | 1050 | 1010 | 23.86% | 21.99%
RTU-3 | KITCHEN | 4400 | 4351 | 3375 | 3321 | 1025 | 1030 | 23.3% | 23.67%
MUA-1 | HOOD SUPPLY | [8 empty] | 4880 | 4750
EF-1 | HOOD 1 | [10 empty] | 2415 | 2373
EF-2 | HOOD 2 | [10 empty] | 1915 | 1872
EF-3 | HOOD 3 | [10 empty] | 1480 | 1476
EF-4 | HOOD 4 | [10 empty] | 1050 | 1068
EF-5 | RESTROOM | [12 empty] | 450 | 439
TOTALS |  | 13200 | 13385 | 10075 | 10245 | 3125 | 3140 |  |  | 4880 | 4750 | 6860 | 6789 | 450 | 439
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 8005 | 7890 |  | FRONT |  | 0.0085 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 7310 | 7228 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 695 | 662 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0085 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Strong winds when testing building pressure disrupted the readings being taken at exterior doors. After taking multiple readings building pressure averaged out to +0.0085" when comparing all equipment on, to all equipment off.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0