## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 3731 | 3250 | 2957 | 750 | 774 | 18.75% | 20.75%
RTU-2 | KITCHEN | 2670 | 2892 | 2170 | 2373 | 500 | 519 | 18.73% | 17.95%
MUA-1 | HOOD 1 | [8 empty] | 1280 | 1229
EF-1 | HOOD 1 | [10 empty] | 1600 | 1812
EF-2 | HOOD 2 | [10 empty] | 500 | 471
EF-3 | RESTROOMS | [12 empty] | 300 | 302
TOTALS |  | 6670 | 6623 | 5420 | 5330 | 1250 | 1293 |  |  | 1280 | 1229 | 2100 | 2283 | 300 | 302
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2530 | 2522 |  | FRONT |  | -0.001 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2400 | 2585 |  | SIDE |  | 0 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 130 | -63 |  | REAR |  | -0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.00066667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Building pressure was not impacted during hood testing as MAU supply air was tested at varying volumes. Suspect building leakage.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0