## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3410 | 2900 | 2903 | 500 | 507 | 14.71% | 14.87%
RTU-2 | DINING ROOM | 4000 | 4043 | 3000 | 3037 | 1000 | 1006 | 25% | 24.88%
MUA-1 | HOOD MAKE UP | [8 empty] | 1300 | 1369
EF-1 | Grease Fan | [10 empty] | 2550 | 2479
EF-2 | RESTROOMS | [12 empty] | 150 | 155
TOTALS |  | 7400 | 7453 | 5900 | 5940 | 1500 | 1513 |  |  | 1300 | 1369 | 2550 | 2479 | 150 | 155
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2882 |  | FRONT |  | -0.004 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2700 | 2634 |  | SIDE |  | -0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | 248 |  | REAR |  | -0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0036667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
BUILDING PRESSURE WITH ALL EQUIPMENT OFF IS -0.007". NET PRESSURE IS -0.0037" BUILDING IS ADJACENT TO AN URGENT CARE FACILITY AND POSSIBLE EXHAUST/RETURN LEAKAGE
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0