## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2400 | 2382 | 2100 | 2065 | 300 | 317 | 12.5% | 13.31%
RTU-2 | DINING | 2400 | 2222 | 2100 | 1921 | 300 | 301 | 12.5% | 13.55%
DOAS-1 | KITCHEN | 2200 | 2297 | 0 | 0 | 2200 | 2297 | 100% | 100%
KEF-1 | HOOD | [10 empty] | 1600 | 1563
KEF-2 | HOOD | [10 empty] | 775 | 763
EF-1 | RESTROOM | [12 empty] | 225 | 213
TOTALS |  | 7000 | 6901 | 4200 | 3986 | 2800 | 2915 |  |  | 0 | 0 | 2375 | 2326 | 225 | 213
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2915 |  | FRONT |  | 0.0044 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2600 | 2539 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 200 | 376 |  | REAR |  | 0.0127 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00855 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0