## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 7672 | 6000 | 5535 | 2000 | 2137 | 25% | 27.85%
AC-2 | DINING A | 3150 | 3358 | 2400 | 2567 | 750 | 791 | 23.81% | 23.56%
AC-3 | S. DINING B | 4000 | 3831 | 3000 | 2861 | 1000 | 970 | 25% | 25.32%
AC-4 | N. DINING B | 2765 | 2902 | 2165 | 2250 | 600 | 652 | 21.7% | 22.47%
AC-5 | DINING | 1800 | 1770 | 1500 | 1472 | 300 | 298 | 16.67% | 16.84%
EF-1 | HOOD 1 RIGHT | [10 empty] | 1085 | 1133
EF-2 | HOOD 1 LEFT | [10 empty] | 1085 | 1096
EF-3 | HOOD 2 | [10 empty] | 700 | 718
EF-4 | HOOD 3 | [10 empty] | 390 | 430
EF-6 | RESTROOM | [12 empty] | 500 | 510
TOTALS |  | 19715 | 19533 | 15065 | 14685 | 4650 | 4848 |  |  | 0 | 0 | 3260 | 3377 | 500 | 510
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4848 |  | FRONT |  | 0.0142 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3760 | 3887 |  | SIDE |  | 0.0135 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 890 | 961 |  | REAR |  | 0.013 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.013567 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390