## ERV-1
National TAB
Project: Cabarrus County Behavioral Health
Address: 1000 Progress Place NE Concord, NC 28025
Asset: ERV-1
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | YORK |  | Manufacturer | YORK
Model Number | XTI-33X60 |  | Model Number | XTI-33X60
Serial Number |  |  | Serial Number
Configuration |  |  | Configuration
No. Pre Filters / Size | 4 / 20X24X2 |  | No. Pre Filters / Size | 4 / 20X24X2
Motor Data |  |  | Motor Data
Motor MFG / Frame | BALDOR / 184T |  | Motor MFG / Frame | BALDOR / 184T
Horsepower / RPM | 5.0 / 1800 |  | Horsepower / RPM | 5.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 6.6 / 1.15 |  | Rated Amperage / SF | 6.6 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 3600 |  | Total CFM | 3600
Fan RPM | 2532 |  | Fan RPM | 2631
VFD Speed | 84.4 |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 6.6 |  | RL Amperage | 6.6
Motor B.H.P. | 3.18 |  | Motor B.H.P. | 3.58
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.82 |  | Total SP | 4.30
Cooling Coil P.D. |  |  | Cooling Coil P.D.
Heating Coil P.D. |  |  | Heating Coil P.D.
Heat Exchanger P.D. |  |  | Heat Exchanger P.D.
Heat Wheel P.D. | 1.00 |  | Heat Wheel P.D.
Pre Filters P.D. | 0.12 |  | Pre Filters P.D.
Total ESP | 1.50 |  | Total ESP | 2.00
EAT Summer DB / WB | 94 / 75 |  | EAT Summer DB / WB
LAT Summer DB / WB | 82 / 68 |  | LAT Summer DB / WB
EAT Winter DB / WB | 21 / 21 |  | EAT Winter DB / WB
LAT Winter DB / WB | 49 / 45 |  | LAT Winter DB / WB

## ERV-2
National TAB
Project: Cabarrus County Behavioral Health
Address: 1000 Progress Place NE Concord, NC 28025
Asset: ERV-2
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | YORK |  | Manufacturer | YORK
Model Number | XTI-33X66 |  | Model Number | XTI-33X66
Serial Number |  |  | Serial Number
Configuration |  |  | Configuration
No. Pre Filters / Size | 2 / 20X24X2 |  | No. Pre Filters / Size | 2 / 20X24X2
| 4 / 20X16X2 |  |  | 4 / 20X16X2
Motor Data |  |  | Motor Data
Motor MFG / Frame | BALDOR / 145T |  | Motor MFG / Frame | BALDOR / 145T
Horsepower / RPM | 2@ 2.0 / 1800 |  | Horsepower / RPM | 2@ 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 2.9 / |  | Rated Amperage / SF | 2.9 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 3900 |  | Total CFM | 3536
Fan RPM | 2405 |  | Fan RPM | 2389
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 2.90 |  | RL Amperage | 2.9
Motor B.H.P. | 1.69 |  | Motor B.H.P. | 1.60
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.79 |  | Total SP | 3.86
Cooling Coil P.D. |  |  | Cooling Coil P.D.
Heating Coil P.D. |  |  | Heating Coil P.D.
Heat Exchanger P.D. |  |  | Heat Exchanger P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Pre Filters P.D. |  |  | Pre Filters P.D.
Total ESP | 1.50 |  | Total ESP | 2.00
EAT Summer DB / WB | 94 / 75 |  | EAT Summer DB / WB
LAT Summer DB / WB |  |  | LAT Summer DB / WB
EAT Winter DB / WB | 21 / 21 |  | EAT Winter DB / WB
LAT Winter DB / WB |  |  | LAT Winter DB / WB

## ERV-3
National TAB
Project: Cabarrus County Behavioral Health
Address: 1000 Progress Place NE Concord, NC 28025
Asset: ERV-3
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | YORK |  | Manufacturer | YORK
Model Number | XTI-33X66 |  | Model Number | XTI-33X66
Serial Number |  |  | Serial Number
Configuration |  |  | Configuration
No. Pre Filters / Size | 2 / 20X24X2 |  | No. Pre Filters / Size | 2 / 20X24X2
| 4 / 20X16X2 |  |  | 4 / 20X16X2
Motor Data |  |  | Motor Data
Motor MFG / Frame | BALDOR / 182T |  | Motor MFG / Frame | BALDOR / 182T
Horsepower / RPM | 2@3.0 / 1800 |  | Horsepower / RPM | 2@3.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 60 / 3
Rated Amperage / SF | 4.2 / |  | Rated Amperage / SF | 4.2 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 5800 |  | Total CFM | 5256
Fan RPM | 2615 |  | Fan RPM | 2541
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 4.20 |  | RL Amperage | 4.20
Motor B.H.P. | 2.74 |  | Motor B.H.P. | 2.48
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.20 |  | Total SP | 4.16
Cooling Coil P.D. |  |  | Cooling Coil P.D.
Heating Coil P.D. |  |  | Heating Coil P.D.
Heat Exchanger P.D. |  |  | Heat Exchanger P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Pre Filters P.D. |  |  | Pre Filters P.D.
Total ESP | 1.50 |  | Total ESP | 2.00
EAT Summer DB / WB | 94 / 75 |  | EAT Summer DB / WB
LAT Summer DB / WB |  |  | LAT Summer DB / WB
EAT Winter DB / WB | 21 / 21 |  | EAT Winter DB / WB
LAT Winter DB / WB |  |  | LAT Winter DB / WB

## ERV-4
National TAB
Project: Cabarrus County Behavioral Health
Address: 1000 Progress Place NE Concord, NC 28025
Asset: ERV-4
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | YORK |  | Manufacturer | YORK
Model Number | XTI-30X51 |  | Model Number | XTI-30X51
Serial Number |  |  | Serial Number
Configuration |  |  | Configuration
No. Pre Filters / Size | 4 / 16X20X2 |  | No. Pre Filters / Size | 4 / 16X20X2
Motor Data |  |  | Motor Data
Motor MFG / Frame | BALDOR / 145T |  | Motor MFG / Frame | BALDOR / 143T
Horsepower / RPM | 3.0 / 3600 |  | Horsepower / RPM | 2.0 / 3600
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 3.80 / |  | Rated Amperage / SF | 2.50 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 1300 |  | Total CFM | 1180
Fan RPM | 2664 |  | Fan RPM | 3355
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 3.80 |  | RL Amperage | 2.50
Motor B.H.P. | 0.94 |  | Motor B.H.P. | 1.07
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 2.70 |  | Total SP | 3.43
Cooling Coil P.D. |  |  | Cooling Coil P.D.
Heating Coil P.D. |  |  | Heating Coil P.D.
Heat Exchanger P.D. |  |  | Heat Exchanger P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Pre Filters P.D. |  |  | Pre Filters P.D.
Total ESP | 1.50 |  | Total ESP | 2.00
EAT Summer DB / WB | 94 / 75 |  | EAT Summer DB / WB
LAT Summer DB / WB |  |  | LAT Summer DB / WB
EAT Winter DB / WB | 21 / 21 |  | EAT Winter DB / WB
LAT Winter DB / WB |  |  | LAT Winter DB / WB