## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2000 | 2064 | 525 | 628 | 1475 | 1436 | 73.75% | 69.57%
RTU-2 | DINING | 2200 | 2118 | 925 | 726 | 1275 | 1392 | 57.95% | 65.72%
KEF-1 | GRILL | [10 empty] | 1050 | 1115
KEF-2 | OVEN | [10 empty] | 600 | 574
KEF-3 | FRYER | [10 empty] | 800 | 826
EF-1 | WOMEN RR | [10 empty] | 75 | 124
EF-2 | MENS RR | [10 empty] | 150 | 154
TOTALS |  | 4200 | 4182 | 1450 | 1354 | 2750 | 2828 |  |  | 0 | 0 | 2675 | 2793 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2750 | 2828 |  | FRONT |  | 0.0001 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2675 | 2793 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 75 | 35 |  | REAR |  | 0.0001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0001 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0