## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2024-08-19 | Store#: | 1994 | Address: | 305 S Eastwood Dr Woodstock, IL
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | RTU/ROOF |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | IF NEAREST EDGE OF RTU IS <10' FROM THE EDGE OF THE ROOF PROVIDE DISTANCE BETWEEN THE TWO EDGES (in) | DOES ROOF HAVE A PARAPET? (Y/N) | DOES RTU/HVAC EQUIPMENT UTALIZE OSHA ROOFTOP GUARD RAILS? (Y/N) | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | FRONT SALES / OFFICE | 09/2005 |  | Carrier | 48HJD014H--55787 | 0905G11557 | EVAP COIL IS DIRTY / HAIL DAMAGE / GENERAL WEAR DUE TO AGE |  | 10 | NATURAL GAS | 224000 / 66 | Not at Unit, Unable to access duct |  | Y | 208 / 230 | 214/213/213 | 3 |  | Y | N | NO | 86x55 | 88x58
RTU 2 | CENTER SOUTH SALES | 07/2005 |  | Carrier | 48HJD008--55702 | 0705G11509 | EVAP COIL IS DIRTY / HAIL DAMAGE / GENERAL WEAR DUE TO AGE |  | 6.5 | NATURAL GAS | 125000 / 37 | Not at Unit, Unable to access duct |  | Y | 208/230 | 213/213/213 | 3 |  | Y | N | NO | 86x55 | 88x58
RTU 3 | CENTER NORTH SALES | 11/2005 |  | Carrier | 48HJE014--55805 | 1105G40703 | EVAP COIL IS DIRTY / HAIL DAMAGE / UNIT CALLING FOR HEAT DURING SURVEY VISIT (75 degrees out) |  | 10 | NATURAL GAS | 250000 / 73 | Unit | Return | Y | 208/230 | 214/215/216 | 3 |  | Y | N | NO | 86x55 | 88x58
RTU 4 | PHARMACY | 07/2005 |  | Carrier | 48JD005H--55702 | 0705G10392 | EVAP COIL IS DIRTY / HAIL DAMAGE / COMPRESSOR BEING REPLACED AT TIME OR SURVEY |  | 4 | NATURAL GAS | 72000 / 21 | Not at Unit, Unable to access duct |  | Y | 208/230 | 212/212/213 | 3 | 66" (OA HOOD) 82" (Unit) | Y | N | NO | 74x42 | 75x45
RTU 5 | LOADING DOCK | 07/2005 |  | Carrier | 48HJE004H--55702 | 0705G10405 | EVAP COIL IS DIRTY / HAIL DAMAGE / GENERAL WEAR DUE TO AGE |  | 3 | NATURAL GAS | 72000 / 21 | Not at Unit, Unable to access duct |  | Y | 208/230 | 212/213/213 | 3 | 94" (OA HOOD) | Y | N | NO | 74x42 | 75x45
RTU 6 | PHOTO | 07/2005 |  | Carrier | 48HJE004H--55702 | 0705G10404 | EVAP COIL IS DIRTY / HAIL DAMAGE / GENERAL WEAR DUE TO AGE |  | 3 | NATURAL GAS | 72000 / 21 | Not at Unit, Unable to access duct |  | Y | 208/230 | 213/213/213 | 3 | 90" | Y | N | NO | 74x42 | 75x45
RTU 7
EH | ENTRANCE | 05/2005 |  | REZNOR | HRPB150-8-S-2 | EBEE66X2N03411 | DISCONNECT OFF AT ROOF / APPEARS IN WORKING ORDER |  |  | NATURAL GAS |  | Not at Unit, Unable to access duct |  | Y | 208 | 214/213/213 | 3 |  | Y | N | NO | 90x35 | 87x34
SPLIT SYSTEM DATA
CU 1 | [6 empty] | *include line set sizes*
CU 2 | [6 empty] | *include line set sizes*
CU 3 | [6 empty] | *include line set sizes*
AHU 1
AHU 2
AHU 3
EVAPORATIVE COOLER/SWAMP COOLER
VENTILATION DATA
ERV 1
ERV 2
STOCK ROOM SF
STOCK ROOM EF
EF 1 | Pharmacy | 2013-10-01 | ROOF MOUNTED | LOREN COOK | 90 ACEH | 006SE88969-00 | NOT OPERATING / SOME DIRT ON FAN CAGE | [7 empty] | 115 | 0 | 1 | 48" | Y | N | NO | 17.5x17.5 | 18x18
EF 2 | Restroom | 2006-09-01 | ROOF MOUNTED | LOREN COOK | 90ACEH | 006S910160-00 | SOME DIRT BUILDUP ON HOUSING / WIRE COVER MISSING INSIDE HOUSING | [7 empty] | 115 | 121 | 1 | 120" | Y | N | NO | 17.5x17.5 | 18x18
EF 3
EF 4
EF 5
EF 6
EF 7
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | N | [5 empty] | RTU-1 | Breaker | Siemens | No Model Listed | 100 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1.5"
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) | NONE |  | Provid partner name |  |  |  | RTU-2 | Breaker | Siemens | NL | 60 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1"
If Partner Tenant Exists do they have full height walls? (Y/N) | NA |  | Full height walls are defined as walls up to ceiling. |  |  |  | RTU-3 | Breaker | Siemens | NL | 100 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1.5"
Obvious "non-typical" Heat Load (Y/N) provide detail in note section | N |  | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | RTU-4 | Breaker | Siemens | NL | 30 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1"
Tenant Space (Y/N): | N |  | Tenant Name (VMD/Kroger/LabCorp, etc.):
Photo Lab (Y/N): | Y |  | Dry/Wet Lab: Dry |  |  |  | RTU-5 | Breaker | Siemens | NL | 30 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1"
Roof Condition (Good/Fair/Poor): | F | [5 empty] | RTU-6 | Breaker | Siemens | NL | 30 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1"
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | Galvanized |  | If "Other" Specify Type: |  |  |  | UH-1 | Breaker | Siemens | NL | 60 | WIRE LABEL WORN / UNABLE TO DETERMINE | 1"
Unit Hail Damage (Y/N): | Y | [5 empty] | CU 1
Store within 20 Miles of Ocean? (Y/N): | N | [5 empty] | CU 2
Existing EMS (Y/N): | Y |  | EMS Type(FSG/Gridpoint): GRIDPOINT |  |  |  | CU 3
Fire Alarm Panel Operational (Y/N): | Y |  | Panel Model#: 5820 XL (IntelliKnight) P/N: 151210E |  |  |  | AHU 1
Photo of Fire Alarm Panel Taken (Y/N): | Y | [5 empty] | AHU 2
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | REMOTE CONDENSING | [5 empty] | AHU 3
Main Refridgeration Type (Walk-In or Reach-In) | Freezer:WALK-IN | [5 empty] | EVAPORATIVE COOLER/SWAMP COOLER
| Cooler:WALK-IN | [5 empty] | STOCK ROOM SF
Self-Contained Refrigeration ONLY Door Count: | Freezer: NA | [5 empty] | STOCK ROOM EF
Cooler: NA
Obvious Visual Damage to MDP (Y/N): | N |  | Explain Visual Damage:
Notes for Installer:
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type | Standard | Standard | Standard | Standard | Standard | Standard |  | Standard
A (Length) | 86" | 86" | 86" | 74" | 74" | 74" |  | 90"
B (Width) | 55" | 55" | 55" | 42" | 42" | 42" |  | 35"
E
F
G
H
I
J
K
L
M
N
O