## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 2975 | 2868 | 2422 | 2148 | 553 | 720 | 18.59% | 25.1%
RTU-2 | SALES/OFFICE | 2975 | 2927 | 2422 | 2242 | 553 | 685 | 18.59% | 23.4%
RTU-3 | SALES | 1750 | 1597 | 1650 | 1487 | 100 | 110 | 5.714% | 6.888%
RTU-4 | SALES/BREAK ROOM | 1750 | 1582 | 1650 | 1476 | 100 | 106 | 5.714% | 6.7%
RTU-5 | PHARMACY | 1400 | 1482 | 1400 | 1482 | 0 | 0 | 0% | 0%
RTU-6 | RECEIVING | 1400 | 1526 | 1300 | 1425 | 100 | 101 | 7.143% | 6.619%
EF-1 | OFFICE | [12 empty] | 300 | 213
EF-2 | EMPLOYEE RR | [12 empty] | 300 | 281
EF-3 | MENS RR | [12 empty] | 250 | 242
EF-4 | WOMENS RR | [12 empty] | 250 | 255
EF-5 | PHOTO
TOTALS |  | 12250 | 11982 | 10844 | 10260 | 1406 | 1722 |  |  | 0 | 0 | 0 | 0 | 1100 | 991
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1406 | 1722 |  | FRONT |  | 0.0138 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1100 | 991 |  | SIDE |  | 0.0156 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 306 | 731 |  | REAR |  | 0.0141 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0145 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
UNABLE TO LOWER OA FROM RTU 1 & 2 TO DESIGN. ANY CHANGE BELOW 20% DAMPERS FULLY CLOSE. SET AT 20% WHEN READINGS WERE TAKEN.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0