## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | DINING | 4200 | 4412 | 3150 | 3334 | 1050 | 1078 | 25% | 24.43%
AHU-2 | KITCHEN | 2950 | 2964 | 2400 | 2430 | 550 | 534 | 18.64% | 18.02%
AHU-3 | BOH |  |  |  |  | 25 | 0 | #DIV/0! | #DIV/0!
AHU-4 | WAREWASH |  |  |  |  | 25 | 0 | #DIV/0! | #DIV/0!
EF-1 | KITCHEN HOOD | [10 empty] | 1550 | 1496
EF-2 | RESTROOMS | [12 empty] | 290 | 276
EF-3 | GENERAL | [12 empty] | 650 | 682
TOTALS |  | 7150 | 7376 | 5550 | 5764 | 1650 | 1612 |  |  | 0 | 0 | 1550 | 1496 | 940 | 958
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1650 | 1612 |  | FRONT |  | -0.01 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2490 | 2454 |  | SIDE |  | -0.009 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -840 | -842 |  | REAR |  | -0.011 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.01 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Building pressure with EF-3 disabled: -0.002"
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0