## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 4451 | 3860 | 3323 | 1140 | 1128 | 22.8% | 25.34%
RTU-2 | KITCHEN | 5000 | 5041 | 2370 | 2452 | 2630 | 2589 | 52.6% | 51.36%
FC-1 | MANAGERS OFFICE |  |  |  |  | 0 | 0 | #DIV/0! | #DIV/0!
EF-1 | HOOD 1 | [10 empty] | 1400 | 1383
EF-2 | HOOD 2 | [10 empty] | 1385 | 1341
EF-3 | RESTROOMS | [12 empty] | 400 | 358
TOTALS |  | 10000 | 9492 | 6230 | 5775 | 3770 | 3717 |  |  | 0 | 0 | 2785 | 2724 | 400 | 358
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3770 | 3717 |  | FRONT |  | 0.0027 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3185 | 3082 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 585 | 635 |  | REAR |  | 0.0053 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2630 | 2589
TOTAL KITCHEN EXHAUST |  | 2785 | 2724
NET AIRFLOW |  | -155 | -135
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0