## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4400 | 4316 | 3350 | 3287 | 1050 | 1029 | 23.86% | 23.84%
RTU-2 | BAR AND DINING | 4400 | 4388 | 3350 | 3362 | 1050 | 1026 | 23.86% | 23.38%
RTU-3 | KITCHEN | 4400 | 4397 | 3375 | 3382 | 1025 | 1015 | 23.3% | 23.08%
MUA-1 | KITCHEN HD | [8 empty] | 4880 | 4869
EF-1 | KITCHEN HD 1 | [10 empty] | 1480 | 1500
EF-2 | KITCHEN HD 2 | [10 empty] | 2125 | 2128
EF-3 | KITCHEN HD 3 | [10 empty] | 2205 | 2159
EF-4 | KITCHEN HD 4 | [10 empty] | 1050 | 1060
EF-5 | RESTROOMS | [12 empty] | 450 | 454
TOTALS |  | 13200 | 13101 | 10075 | 10031 | 3125 | 3070 |  |  | 4880 | 4869 | 6860 | 6847 | 450 | 454
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 8005 | 7939 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 7310 | 7301 |  | SIDE |  | 0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 695 | 638 |  | REAR |  | 0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0036667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0