## Report Sheet
STORE #: | 4436 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | Youngstown, OH. | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-06-14 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | Dylan Crisman | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZF102N18R2A1AAA1A2 | N2H2846418 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1760 | 1760 | 925 | 952 | 3 | 210.3 | 210.3 | 3 | 8.3 | 6.43 | 6.43 | 2.2604 | 2.2604 | 0%
YORK | ZF120N24R2A1AAA1A3 | N2H2934743 | RTU-2 | DINING | 1000 | 422 | 1000 | 995 |  | 1748 | 1748 | 972 | 970 | 3 | 210.5 | 210.5 | 3 | 8.3 | 6.86 | 7.5 | 2.4139 | 2.6391 | 9.329%
CAPTIVE AIRE | A1-D.250-15D | 5475601 | MUA-1 | HOOD 1 | 1950 | 1724 | 1700 | 1724 | No | 2163 | 2163 | 2163 | 2163 | 2 | 188 | 188 | 3 | 5.48 | 5 | 5 | 1.5713 | 1.5713 | 0%
CAPTIVE AIRE | DU240HFA | 5475601 | EF-1 | HOOD 1 | 3200 | 3369 | 2450 | 2505 | No | 764 | 568 | 764 | 568 | 3 | 110 | 62 | 3 | 9.2 | 5.8 | 4.2 | 1.0665 | 0.43529 | -59.18%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2146 | 2700 | 2719 |  | FRONT DOOR |  | 0.0234 |  |  | INITIAL | 7.3122 | 2146
|  |  | TOTAL EXHAUST |  | 3350 | 3519 | 2600 | 2655 |  | BACK DOOR |  | 0.023 |  |  | FINAL | 6.9062 | 2719
|  |  | NET AIRFLOW |  | 100 | -1373 | 100 | 64 |  | AVERAGE |  | 0.0232 |  |  | ∆ | -0.40601 | 573
Issue List
Unit # | Description
MUA-2 | MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.