## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 3968 | 2855 | 2781 | 1145 | 1187 | 28.62% | 29.91%
RTU-2 | KITCHEN | 5000 | 4979 | 2500 | 2370 | 2500 | 2609 | 50% | 52.4%
KEF-1 | HOOD-1 | [10 empty] | 700 | 678
KEF-2 | HOOD-2 | [10 empty] | 700 | 715
KEF-3 | HOOD-3 | [10 empty] | 700 | 719
KEF-4 | HOOD-4 | [10 empty] | 700 | 661
EF-5 | RESTROOMS | [12 empty] | 200 | 210
TOTALS |  | 9000 | 8947 | 5355 | 5151 | 3645 | 3796 |  |  | 0 | 0 | 2800 | 2773 | 200 | 210
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3645 | 3796 |  | FRONT |  | -0.015 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3000 | 2983 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 645 | 813 |  | REAR |  | 0.019 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.002 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1145 | 1187
TOTAL KITCHEN EXHAUST |  | 2800 | 2773
NET AIRFLOW |  | -1655 | -1586
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0