	Monday, September 28, 2020
	Quote #: 4532549
	Ministries 25



	(513) 860-5555 

	WWW.CAPTIVEAIRE.COM 



	


	[image: image1.jpg]ONE SYSTEM: ONESOURCE

CAPTIVEARE | QUOTE






	Monday, September 28, 2020 

	Quote# 4532549 - Ministries 25 



	


	To: 

Chip Glaesher

F.G. SCHAEFER CO, INC/NAFED

P.O. Box 12517

Florence, SC 29504

Phone: (513) 591-0209

cglaescher@fgschaefer.com
	From: 

Austin McFall

CaptiveAire Systems

1329 East Kemper Rd.

Ste. 4210

Cincinnati, OH 45246

Phone: (513) 860-5555

reg120@captiveaire.com
	Ship To: 

CINCINNATI, OH 45242



	


	CaptiveAire Systems proposes to furnish the following equipment. Production of listed items will commence upon receipt of an approved proposal, a purchase order, an approved submittal and approved credit. 


	EQUIPMENT: 



	Hood #1 - HD1 - Job #4532549

	5424ND-2-PSP-F - 10ft 9" Long Exhaust-Only Wall Canopy Hood with 12" Wide Front Perforated Supply Plenum with Built-in 3" Back Standoff
	 
	x1
	 

	- 430 SS Where Exposed
	
	x1 
	

	- Fire Cabinet on the Right Side 12.00" Width x 54.00" Length x 24.00" Height (Additional charges may apply for cabinet if not sold with fire system)
	
	x1 
	

	- FILTER - 16" tall x 16" (15.625" by 15.625") wide Stainless Steel Captrate Solo filter with hook, ETL Listed. Particulate capture efficiency: 85% efficient at 9 microns, 76% efficient at 5 microns. Used on hoods shipped AFTER 7/27/17.
	
	x8 
	

	- L55 Series E26 Canopy Light Fixture - High Temp Assembly, Includes Clear Thermal and Shock Resistant Globe (L55 Fixture), Bulbs By Others
	
	x4 
	

	- Extra Fixtures- L55 Series E26 Canopy Light Fixture - High Temp Assembly, Includes Clear Thermal and Shock Resistant Globe (L55 Fixture)
	
	x1 
	

	- EXHAUST RISER - Factory installed 14" Diameter X 4" Height
	
	x1 
	

	- SUPPLY RISER - 10"x 24" Supply Riser with Volume Dampers
	
	x3 
	

	- 1/2 Pint Grease Cup New Style, Flanged Slotted
	
	x2 
	

	- FIELD WRAPPER 17.00" High Front, Left, Right
	
	x1 
	

	- Electrical Package Installation in Utility Cabinet by Plant.
	
	x1 
	

	- BACKSPLASH 80.00" High X 141.00" Long 430 SS Vertical (Includes End Caps & Divider Bars)
	
	x1 
	

	- BACKSPLASH 120.00" High X 48.00" Long 430 SS Vertical (BS LEFT) (Includes End Caps & Divider Bars)
	
	x1 
	

	- BACKSPLASH 120.00" High X 36.00" Long 430 SS Vertical (BS RIGHT) (Includes End Caps & Divider Bars)
	
	x1 
	

	- RIGHT QUARTER END PANEL 23" Top Width, 0" Bottom Width, 23" High 430 SS
	
	x1 
	

	- LEFT QUARTER END PANEL 23" Top Width, 0" Bottom Width, 23" High 430 SS
	
	x1 
	

	- Parts required to mount riser sensor on riser with 3 inch insulation double wall duct.
	
	x1 
	


	Fire System #1 - FS1 - Job #4532549 (INCLUDES INSTALL, PERMIT, TEST & GAS VALVE FOR SYSTEM)

	ANSUL-3.0 Ansul 3 gallon Fire System in Utility Cabinet (includes pre-piped hood(s) with detection, tank(s), release mechanism, microswitches and pull station).
Includes piping for hood: 1.
	 
	x1
	 

	- MGVA2 GAS VALVE - 2" Mechanical Shutoff Valve (Ansul)(28-55610) - Includes Upstream Strainer assembly
	
	x1 
	


	Fan #1 DU85HFA - Exhaust Fan (KEF1) - Job #4532549

	DU85HFA High Speed Direct Drive Centrifugal Upblast Exhaust Fan with speed control (speed control included for single phase only), disconnect switch and 15-3/4" wheel.
Exhaust Fan handles 1935 CFM @ -1.200" wc ESP, Fan runs at 1498 RPM.
Exhaust Motor: 1.000 HP, 1 Phs, 115 V, 60Hz, 11.6 FLA, TEAO-ECM (Totally Enclosed Air Over Electronically Commutated Motor)
	 
	x1
	 

	- Grease Cup for kitchen-duty centrifugal exhaust fans,
Box Dimensions 17-1/8 L X 5-1/16 W X 3-3/4 H (20 GA.) (Includes Down Spout)
	
	x1 
	

	- ECM Wiring Package for exhaust motors with PWM signal from ECPM03 prewire.
	
	x1 
	

	- Insulated Heat Baffle for Exhaust Fans. Type 475FRK 1 inch thick insulation installed on the top side of the top plate and under the motor of upblast and downblast fans. Cut to fit shaft wrapper and around vibration isolators and motor cooling hole. Caulked down to top plate.
	
	x1 
	

	- Gasketing - Thermeez Woven Ceramic Tape - 1/4" x 1" with adhesive back - Max Temp 1500°F. To be applied between fan base and grease duct. Installed under fan base 1/2" from the inside edge of the base to match up with the curb top flanges.
	
	x1 
	

	- Multi-Conductor - Single Shielded Twisted Pair Cable, 18 AWG stranded (19x30) TC conductors, plenum, FEP insulation, overall shield (100% coverage), 20 AWG stranded TC drain wire, FEP jacket. Priced per foot. For use with CORE Interlock Network, light dimming 0-10VDC reference signal, and PWM signal from ECPM03 to ECM.
	
	x45 
	

	- KEF1 Curb CRB23x24E On Fan #1 Flat Curb
	
	x1 
	

	- Hinged Base for Curb. Standard Hinge attached to curb. Used on Fans with wheels 20 inches or smaller. 12 GA Galvanized.
	
	x1 
	

	- Vented Base for Curb
	
	x1 
	


	Fan #2 A1-D.250-15D - Heater (HMUA1) - Job #4532549

	A1-D.250-15D Direct Gas Fired Heated Make Up Air Unit with 15" Direct Drive Fan
Supply Fan handles 1548 CFM @ 0.450" wc ESP, Fan runs at 1728 RPM.
Heater supplies 107048 BTUs. 67°F Temperature Rise. [Fuel: Natural Gas]
Supply Motor: 1.000 HP, 1 Phase, 115 V, 60Hz, 11.6 FLA, TEAO-ECM (Totally Enclosed Air Over Electronically Commutated Motor)
Down Discharge - Air Flow Right -> Left
	 
	x1
	 

	- Sloped Filtered Intake for Size #1 Standard Untempered Supply Unit.
22" Wide x 25.875" Long x 23.375" High. 
Includes 2" MV EZ Kleen Metal Mesh Filters.
	
	x1 
	

	- RTC Solutions • 40-90°F Discharge Temp Control
	
	x1 
	

	- Gas Manifold for DF1 GM - BTU 0 - 550001 - 7 in. w.c. - 14 in. w.c., No Insurance Requirement (ANSI), BV250-66
	
	x1 
	

	- Motorized Back Draft Damper 16" X 18" for Size 1 Standard & Modular Heater Units w/Extended Shaft, Standard Galvanized Construction, 3/4" Rear Flange, Low Leakage, TFB120S Actuator Included
	
	x1 
	

	- Low Fire Start. Allows the burner circuit to energize when the modulation control is in a low fire position.
	
	x1 
	

	- Gas Pressure Gauge, 0-35", 2.5" Diameter, 1/4" Thread Size
	
	x1 
	

	- Gas Pressure Gauge, -5 to +15 Inches Wc., 2.5" Diameter, 1/4" Thread Size
	
	x1 
	

	- ECM Wiring Package for supply motors with PWM signal from ECPM03 prewire.
	
	x1 
	

	- Multi-Conductor - Single Shielded Twisted Pair Cable, 18 AWG stranded (19x30) TC conductors, plenum, FEP insulation, overall shield (100% coverage), 20 AWG stranded TC drain wire, FEP jacket. Priced per foot. For use with CORE Interlock Network, light dimming 0-10VDC reference signal, and PWM signal from ECPM03 to ECM.
	
	x40 
	

	- HMUA1 Curb CRB21X71X16INS Insulated On Fan #2 Flat Curb
	
	x1 
	

	- Full Bottom Curb Corner. Base flange corners fully welded or staked by factory.
	
	x1 
	


	Electrical System #1 - EP1 - Job #4532549

	SC-111110FP 120V 1 Phase w/ control for 1 Exhaust Fan, 1 Supply Fan, Exhaust on in Fire, Lights out in Fire, Fan(s) On/Off Thermostatically Controlled. Room temperature sensor shipped loose for field installation. Includes 1 Duct Thermostat kit.
	 
	x1
	 

	- Digital Prewire Lighting Relay Kit. Includes hood lighting relay & terminal blocks. Allows for up to 1400W of lighting each.
	
	x1 
	

	- Thermistor CABLE - 18/2 AWG GREEN WHITE, plenum rated. USED for thermistor duct stat. Per Foot Price.
	
	x50 
	


	Factory Services
	 
	 
	 

	Service Design Verification for Direct Fired Heater
	 
	x1
	 

	Service Design Verification for Exhaust Fan
	 
	x1
	 

	Service Design Verification for Hood
	 
	x1
	 

	Service Design Verification for Standard Electrical Control Package
	 
	x1
	 

	Service Design Verification Mileage Charge: (28) x 2 = 56 total miles
	 
	x1
	 

	
	

	 


	Total Net Price:
	$13,240.39

	Shipping:
	$895.87

	Tax: 
	Not Included


	SERVICE DESIGN VERIFICATION DISCLAIMER 


	Field Service Technician is responsible for one trip to site to ensure the above equipment is operating within design specifications. All equipment must be operational. Fire suppression system should be hooked-up and armed. Additional trips will result in charges to be covered by others. 


	INSTALLATION BY OTHERS 


	By Others:
Installation, ductwork, patching, all electrical field wiring, start-up & balance, gas or electric shutdown for fire system hook-up. 

Note:
Customer is responsible for additional labor charges as a result of cooking equipment layout changes after the release of the order, union labor or prevailing wage charges, or additional trips by fire system distributor caused by jobsite delays, permits, fees or test required by local authority. Submittal will specify applicable testing and approval agencies. 
	CaptiveAire Systems requirement for all field hook ups: 
All fire system detection conduit must be half inch EMT. All conduit fittings must be compression type and fully tightened. All conduit ends must be reamed and deburred and blown clear of debris prior to assembly. All conduit must be fully and robustly supported to avoid accidental fire system discharge. 

CaptiveAire Systems product must be installed in accordance with installation instructions provided with equipment or available on our web site at www.captiveaire.com. 

Ductwork must be designed and installed in accordance with AMCA and ASHRAE standards as presented in CaptiveAire Systems "Guide to Designing Air Flow Systems", available here. 

Hood and Ductwork hanging brackets and angles must be supported with 1/2" - 13 TPI grade 5 (minimum) all-thread. Sandwich hanging angles and ceiling anchor points with 1/2" grade 5 (minimum) steel flat washers and 1/2" - 13 TPI grade 5 (minimum) hex nuts. A doubled hex nut configuration must be used beneath hood and duct hanging brackets and above ceiling anchors (single hex nut beneath hanging angle is only acceptable for full length and supply plenum hanging angle types). Maintain 1/4" of exposed threads beneath bottom hex nut. Torque all hex nuts to 57 ft-lbs. Reference the installation manual for additional details and limitations of all structural supports. 


	WARRANTY 


	Standard Product Warranty 

	This equipment is warranted to be free from defects in materials and workmanship, under normal use and service, for a period of 2-years from date of shipment. 

	Warranty Instructions 

	This Standard Product Warranty shall not apply if: 


1. The equipment is not installed by a qualified installer per the MANUFACTURER'S installation instructions shipped with the product. 

2. The equipment is not installed in accordance with federal, state and local codes and regulations. 

3. The equipment is misused or neglected, or not maintained per the MANUFACTURER'S maintenance instructions. 

4. The equipment is not operated within its published capacity. 

5. The invoice is not paid within the terms of the sales agreement. 

The MANUFACTURER shall not be liable for incidental and consequential losses and damages potentially attributable to malfunctioning equipment. Should any part of the equipment prove to be defective in material or workmanship within the Standard Product Warranty, upon examination by the MANUFACTURER, such part will be repaired or replaced by MANUFACTURER at no charge. The BUYER shall pay all labor costs incurred in connection with such repair or replacement. Equipment shall not be returned without MANUFACTURER'S prior authorization and all returned equipment shall be shipped by the BUYER, freight prepaid to a destination determined by the MANUFACTURER. 

NOTE: To receive warranty coverage, register this product by filling out the Start-up and Maintenance Document. Fax the form to 1-919-554-9374 or call 1-866-784-6900 for email information. 


	SHIPPING 


	Freight includes one shipment only, delivered to the job site address listed on this proposal. Customer is responsible for freight charges on any items shipped early. This is an estimated freight charge and is subject to change based on current freight costs when the job is released for production. 


	APPROVAL 


	The above prices, specifications, and conditions are satisfactory and are hereby accepted. You are authorized to perform the work specified. Receipt of the CaptiveAire Systems Terms & Conditions are hereby acknowledged (Form TC101), and by signature hereto, we agree to said Terms & Conditions. Payment will be made in accordance with authorized agreement. Please note, proposal may be withdrawn by CaptiveAire Systems if not accepted within 30 days. 
  



Authorized Signature 

 



Date 

 



Signature 

 



Date 



We accept MasterCard®, VISA®, American Express®, and Discover® cards for immediate credit approval and expedited order processing. 


[image: image2.png]| I
VISA EX Discover

i







	TERMS AND CONDITIONS

	Acceptance: This proposal is submitted for acceptance within 30 days from the date of proposal. Prices are firm after acceptance provided the Buyer releases the order for production within 90 days of placement-see paragraph "prices." Typographical and clerical errors in quotations, orders and acknowledgments are subject to correction.
Terms of Payment: Net thirty (30) days from date of our invoice, unless specified to the contrary and subject to the approval of the Company. A Service Charge of 1.5 % per month may be invoked and applied after the 30 day period until payment is received. Invoicing will be rendered when shipment has been made, unless otherwise indicated in quotation. The stated price is subject to any state, federal or local government regulatory ordinances or statutes governing interest rates and shall be construed and interpreted to allow the highest rate applicable and not more. In the event of a conflict between this rate and other law, the law shall prevail. In the event CaptiveAire Systems employs an attorney to enforce its rights and remedies under this agreement and/or to collect funds owing pursuant to this agreement, buyer agrees to pay a reasonable attorney's fee for CaptiveAire Systems attorney, plus all other reasonable expenses incurred by CaptiveAire Systems in enforcing its rights under this agreement.
Taxes: Unless specifically stated, we include no taxes of any kind in the sale price. Any taxes, if applicable and imposed by any present or future local, state or federal agency for any reason must be paid by the Buyer.
Shipments: All shipments are f.o.b. Factory or, if shipped from another location, f.o.b., point of shipment with charges either allowed, added to invoice, or collect as noted.
Claims: The responsibility of the company ceases upon delivery of material in good order to the carrier. As all goods are shipped at buyer's risk, any claims for damage or shortage or loss in transit must be filed by the buyer against the transportation company, (We will assist the Buyer in any reasonable way possible in the filing and collection for any claim for damages and/or losses while in transit.) Claims against factory shortages will not be considered unless made within 60 days after receipt of the goods.
Acceptance or Approval: Should the equipment on this proposal be purchased subject to acceptance or approval of another (such as Architect, Engineer. Owner, etc.), CaptiveAire Systems shall not be liable in any way should acceptance or approval not be granted. We cannot guarantee to meet or equal specifications written on behalf of another equipment manufacturer.
Warranties: CaptiveAire Systems extends to buyer the manufacturers warranty (a copy of which is available upon request). Manufacturer's warranty is in lieu of any warranties contained in any applicable project conditions, plans, or specifications unless specifically stated otherwise. CaptiveAire Systems makes no other warranties, express or implied, as to any matter whatsoever, including without limitation, the conditions of the equipment, its merchantability or fitness for a particular purpose. CaptiveAire Systems shall not be liable for any damages by reason of failure of the equipment to operate or a faulty operation of this equipment. CaptiveAire Systems shall not be held responsible for any direct, incidental or consequential damages or liquidated damages or losses (including but not limited to loss of use, income, profit or production, or spoilage or increased cost of operation) resulting from the installation, operation or use of the equipment.
Limitation of Remedy: CaptiveAire Systems shall have no liability for any damage caused by negligence, accident, misuse, improper storage, improper installation, improper service, maintenance or operation. CaptiveAire Systems liability (whether under theories of warranty, negligence, strict liability or contract) is limited solely to repair or replacement of the equipment or its parts by CaptiveAire Systems or its duly authorized representative, or at CaptiveAire Systems option and in its sole discretion, refund of the purchase price, and the foregoing shall be the sole and exclusive remedy against CaptiveAire Systems. In no event shall CaptiveAire Systems liability with respect to the goods or their non-delivery exceed the purchase price paid by Buyer to CaptiveAire Systems. Buyer shall have no right to consequential or incidental damages or to any remedy not hereinbefore described. Any claim by Buyer against CaptiveAire Systems with respect to the goods is deemed waived by Buyer unless submitted to CaptiveAire Systems in writing within ten (10) days of the date Buyer discovered or by reasonable inspection should have discovered, the basis for such claim.
Claims Resolution: All claims and disputes between Buyer and CaptiveAire Systems arising out of or relating to performance of any agreement or breach thereof involving this project shall be decided by binding arbitration in accordance with the construction Industry Arbitration rules of the American Arbitration Association (AAA) then existing. Notice of Demand for Arbitration shall be filed in writing by either party to this agreement with the other and with the regional office of the AAA in Charlotte, North Carolina. The procedural and substantive law of the State of North Carolina shall apply in and to all such arbitration proceedings and Raleigh, North Carolina shall be designated as the locale for any such proceedings. Both parties will have the right to conduct discovery in accordance with the Federal Rules of Civil Procedure and within reasonable time limitations to be imposed by the AAA or the arbitrators. Any award arising from such proceedings shall be final and binding upon the parties and enforceable in accordance with the Federal Arbitration Act.
Delays: Seller shall not be liable for failures or delays in making delivery hereunder when such failure or delay results from an act of God or the public enemy accident, explosion, fire, storm, earthquake, flood, drought, perils of the sea, strikes, lock-outs, labor troubles, riots, sabotage, embargo, wars (whether or not declared and whether or not the United States is involved), federal, state or municipal law, ordinance, rule, regulation, order license, priority, seizure requisition or allocation or other restrictions, failure or delay of transportation, shortage of or inability to obtain supplies, equipment, fuel or labor or any other circumstances of a similar or different nature beyond the reasonable control of the Seller.
Credit: If Buyer's credit, at the sole judgment of the Seller, is impaired at any time, Seller shall have the right to defer shipment or cancel the order.
Penalties: No penalty clause of any kind will be effective unless approved in writing by an officer of CaptiveAire Systems.
Cancellations: Should the order be cancelled through no fault of CaptiveAire Systems, the Buyer is liable for reimbursement for any and all expenses incurred in connection with this transaction; and in accordance with law for any other losses incurred by Seller.
Return of Goods: Please take special care to order carefully and completely. All products purchased are custom orders. Custom orders were manufactured in accordance with customer specifications, and therefore, are only returnable per the terms of our RMA policy (http://www.captiveaire.com/sitedocs/returnpolicy.asp). Verify all information before placing the order. Please review policy with your sales consultant prior to purchasing if you have any questions.
Prices: Unless otherwise notified, prices on orders will be held firm provided the order is released for production within 90 days of placement. (The date of placement being the date of the Buyer's order and the date of release being the date the official notice of release is received at the Seller's offices.) Order released after 90 days from date of customer's purchase order may be subject to escalation.
Title: The title to all material(s) and/or equipment and to any and all additions and accessories thereto and substitutions therefore, shall remain with Seller until the purchase price thereof is paid in full.
FORM TC-101 (2/03) 


Page 1 of 2
Page 2 of 3

