## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-T1 | KITCHEN | 9500 | 9405 | 7300 | 7299 | 2200 | 2106 | 23.16% | 22.39%
AC-T2 | MEAL FULFILLMENT | 2830 | 2889 | 2230 | 2293 | 600 | 596 | 21.2% | 20.63%
AC-T3 | DINING | 5000 | 5171 | 3900 | 4056 | 1100 | 1115 | 22% | 21.56%
AC-T4 | OFFICE/TEAM MEMBER | 1800 | 1844 | 1425 | 1486 | 375 | 358 | 20.83% | 19.41%
AC-T5 | BACK OF HOUSE | 1200 | 1268 | 960 | 1027 | 240 | 241 | 20% | 19.01%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1931
EF-2 | HOOD 2 | [10 empty] | 701 | 702
EF-4 | HOOD 3 | [10 empty] | 701 | 708
EF-3 | RESTROOM | [12 empty] | 400 | 408
TOTALS |  | 20330 | 20577 | 15815 | 16161 | 4515 | 4416 |  |  | 0 | 0 | 3315 | 3341 | 400 | 408
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4515 | 4416 |  | FRONT |  | 0.01 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3749 |  | SIDE |  | 0.008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 800 | 667 |  | REAR |  | 0.01 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0093333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390