## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 4100 | 3923 | 4100 | 3923 | 0 | 0 | 0% | 0%
RTU-2 | SALES | 4400 | 4210 | 4400 | 4210 | 0 | 0 | 0% | 0%
RTU-3 | SALES | 4805 | 4435 | 4805 | 4435 | 0 | 0 | 0% | 0%
RTU-4 | SALES | 5000 | 5036 | 5000 | 5036 | 0 | 0 | 0% | 0%
RTU-5 | SALES | 5075 | 5050 | 5075 | 5050 | 0 | 0 | 0% | 0%
RTU-6 | SALES | 5095 | 5106 | 5095 | 5106 | 0 | 0 | 0% | 0%
RTU-7 | SALES | 5000 | 4812 | 5000 | 4812 | 0 | 0 | 0% | 0%
RTU-8 | SALES | 3945 | 4080 | 3945 | 4080 | 0 | 0 | 0% | 0%
RTU-9 | SALES | 3900 | 4042 | 3900 | 4042 | 0 | 0 | 0% | 0%
RTU-10 | PHARMACY | 2515 | 2348 | 2012 | 1854 | 503 | 494 | 20% | 21.04%
RTU-11 | DELI | 2425 | 2462 | 2328 | 2364 | 97 | 98 | 4% | 3.981%
RTU-12 | BAKERY | 1900 | 1945 | 1824 | 1864 | 76 | 81 | 4% | 4.165%
RTU-13 | BACKROOM | 1600 | 1638 | 1392 | 1429 | 208 | 209 | 13% | 12.76%
RTU-14 | BACKROOM | 1600 | 1706 | 1344 | 1430 | 256 | 276 | 16% | 16.18%
RTU-15 | DOCK | 3500 | 3576 | 2765 | 2870 | 735 | 706 | 21% | 19.74%
RTU-16 | BACK OFFICES | 2455 | 2470 | 1988 | 2002 | 467 | 468 | 19.02% | 18.95%
RTU-17 | PICKUP | 3060 | 3017 | 2570 | 2557 | 490 | 460 | 16.01% | 15.25%
RTU-18 | VESTIBLE | 2500 | 2538 | 2350 | 2392 | 150 | 146 | 6% | 5.753%
RTU-19 | VESTIBLE | 2500 | 2600 | 2350 | 2459 | 150 | 141 | 6% | 5.423%
DOAS1 | SALES OA | 4200 | 4040 | 0 | 0 | 4200 | 4040 | 100% | 100%
DOAS2 | SALES OA | 4200 | 4395 | 0 | 0 | 4200 | 4395 | 100% | 100%
EF-4 | HOOD 1 | [10 empty] | 2400 | 2357
EF-9 | BAKERY OVEN | [10 empty] | 600 | 911
EF-10 | BAKERY OVEN | [10 empty] | 600 | 938
EF-1 | CUSTOMER RR | [12 empty] | 700 | 913
EF-2 | FAMILY | [12 empty] | 300 | 311
EF-3 | EMPLOYEE RR | [12 empty] | 500 | 827
EF-5 | ELEC. CLOSET | [12 empty] | 800 | 841
EF-6 | ELECTRICAL | [12 empty] | 800 | 1073
EF-7 | SEAFOOD | [12 empty] | 700 | 818
EF-8 | CLEANING CENTER | [12 empty] | 200 | *1
TOTALS |  | 73775 | 73429 | 62243 | 61915 | 11532 | 11514 |  |  | 0 | 0 | 3600 | 4206 | 4000 | 4783
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 11532 | 11514 |  | FRONT |  | *2 | [8 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 7600 | 8989 |  | SIDE |  | *2 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 3932 | 2525 |  | REAR |  | *2 | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
*1 FAN WAS NOT OPERATIONAL AT TIME OF TESTING. *2UNABLE TO OBTAIN ACCURATE BUILDING PRESSURE DUE TO SOME UNITS NOT BEING OPERATIONAL AND NOT BEING ABLE TO GET ALL RTU'S OPERATING AT HIGH SPEED AT THE SAME TIME.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0