## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN |  | 4768 |  | 4045 |  | 723 |  | 15.16%
RTU-2 | DINING |  | 2120 |  | 1767 |  | 353 |  | 16.65%
MUA-1 | KITCHEN | [9 empty] | 1571
EF-1 | KITCHEN | [11 empty] | 1994
EF-2 | KITCHEN | [11 empty] | 0
EF-3 | RESTROOM | [13 empty] | 110
EF-4 | RESTROOM | [13 empty] | 120
TOTALS |  | 0 | 6888 | 0 | 5812 | 0 | 1076 |  |  | 0 | 1571 | 0 | 1994 | 0 | 230
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  |  | 2647 |  | FRONT |  | 0.012 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  |  | 2224 |  | SIDE |  | 0.008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  |  | 423 |  | REAR |  | 0.015 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.011667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0