## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9808 | 7600 | 7966 | 1900 | 1842 | 20% | 18.78%
AC-2 | DRIVE THRU | 6000 | 6231 | 4800 | 4925 | 1200 | 1306 | 20% | 20.96%
AC-3 | DINING | 6000 | 6250 | 4800 | 5141 | 1200 | 1109 | 20% | 17.74%
AC-4 | TEAM ROOM/OFFICE | 1875 | 1910 | 1375 | 1388 | 500 | 522 | 26.67% | 27.33%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 2029
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1349
EF-3 | RESTROOM | [12 empty] | 375 | 383
TOTALS |  | 23375 | 24199 | 18575 | 19420 | 4800 | 4779 |  |  | 0 | 0 | 3315 | 3378 | 375 | 383
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4800 | 4779 |  | FRONT |  | 0.0108 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3761 |  | SIDE |  | 0.0097 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1110 | 1018 |  | REAR |  | 0.0144 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.011633 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] NOT ALL PADS INSTALLED EXPECTED BUILDING PRESSURE IS GREATER. AC-1 DAMPER MANUALLY SET.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390