## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
ERV-1 | IT/MECHANICAL | 1000 | 1003 | 0 | 0 | 1000 | 1003 | 100% | 100% |  |  |  |  | 950 | 886
ERV-2 | STORAGE 2 | 675 | 645 | 0 | 0 | 675 | 645 | 100% | 100% |  |  |  |  | 500 | 496
EF-1 | RR | [12 empty] | 50 | 53
EF-2 | RR2 | [12 empty] | 50 | 51
EF-3 | STORAGE 2 | [12 empty] | 50 | [1]
TOTALS |  | 1675 | 1648 | 0 | 0 | 1675 | 1648 |  |  | 0 | 0 | 0 | 0 | 1600 | 1486
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1675 | 1648 |  | FRONT |  | 0.0042 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1600 | 1486 |  | SIDE |  | 0.0103 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 75 | 162 |  | REAR |  | 0.0026 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0057 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] : EF-3 IS NOT OPERABLE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0