## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5850 | 6137 | 3950 | 4231 | 1900 | 1906 | 32.48% | 31.06%
RTU-2 | KITCHEN | 6150 | 6211 | 4250 | 4280 | 1900 | 1931 | 30.89% | 31.09%
PRV-2 | HOOD 1 | [10 empty] | 1500 | 1468
PRV-3 | HOOD 2 | [10 empty] | 1500 | 1498
PRV-4 | HOOD 3 | [10 empty] | 350 | 363
PRV-1 | RESTROOMS | [12 empty] | 375 | 369
EF-1A | MOP ROOM | [12 empty] | 75 | 69
TOTALS |  | 12000 | 12348 | 8200 | 8511 | 3800 | 3837 |  |  | 0 | 0 | 3350 | 3329 | 450 | 438
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3800 | 3837 |  | FRONT |  | 0.0061 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3767 |  | SIDE |  | 0.0068 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 70 |  | REAR |  | 0.0041 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0056667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0