## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4500 | 4286 | 3200 | 3104 | 1300 | 1182 | 28.89% | 27.58%
RTU-2 | KITCHEN | 4550 | 4320 | 4200 | 3989 | 350 | 331 | 7.692% | 7.662%
FCU-1 | OFFICE |  |  |  |  | 40 | 47 | #DIV/0! | #DIV/0!
MUA-1 | COOKLINE | [8 empty] | 3316 | 3415
KEF-1 | HOOD 1/2 | [10 empty] | 4144 | 3946
EF-1 | RESTROOMS | [12 empty] | 375 | 380
TOTALS |  | 9050 | 8606 | 7400 | 7093 | 1690 | 1560 |  |  | 3316 | 3415 | 4144 | 3946 | 375 | 380
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5006 | 4975 |  | FRONT |  | 0.0029 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4519 | 4326 |  | SIDE |  | 0.0103 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 487 | 649 |  | REAR |  | 0.0125 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0085667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3666 | 3746
TOTAL KITCHEN EXHAUST |  | 4144 | 3946
NET AIRFLOW |  | -478 | -200
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0