## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 4038 | 3250 | 3269 | 750 | 769 | 18.75% | 19.04%
RTU-2 | DINING | 3400 | 3272 | 2520 | 2413 | 880 | 859 | 25.88% | 26.25%
MUA-1 | KITCHEN HOOD | [8 empty] | 1938 | 2003
EF-1 | KITCHEN HOOD | [10 empty] | 3206 | 3126
EF-2 | RESTROOM | [12 empty] | 150 | 157
TOTALS |  | 7400 | 7310 | 5770 | 5682 | 1630 | 1628 |  |  | 1938 | 2003 | 3206 | 3126 | 150 | 157
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3568 | 3631 |  | FRONT |  | 0.0094 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3356 | 3283 |  | SIDE |  | 0.0113 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 212 | 348 |  | REAR |  | 0.0089 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0098667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1938 |  | 3206 |  | -1268