## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3500 | 3548 | 2600 | 2688 | 900 | 860 | 25.71% | 24.24%
RTU-2 | KITCHEN | 4500 | 4548 | 1970 | 2085 | 2530 | 2463 | 56.22% | 54.16%
KEF-1 | HOOD 1 | [10 empty] | 1575 | 1543
KEF-2 | HOOD 2 | [10 empty] | 1588 | 1529
EF-1 | RESTROOMS | [12 empty] | 300 | 293
TOTALS |  | 8000 | 8096 | 4570 | 4773 | 3430 | 3323 |  |  | 0 | 0 | 3163 | 3072 | 300 | 293
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3430 | 3323 |  | FRONT |  | -0.0009 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3463 | 3365 |  | SIDE |  | -0.0014 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -33 | -42 |  | REAR |  | -0.0009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0010667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0