## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES/ENTRY/OFFICE | 5250 | 3656 | 4465 | 2842 | 785 | 814 | 14.95% | 22.26%
RTU-2 | SALES/PHARM | 4200 | 3619 | 4200 | 2567 | 0 | 1052 | 0% | 29.07%
RTU-3 | SALES/STOCKROOM | 4200 | 2963 | 3570 | 2963 | 630 | 0 | 15% | 0%
RTU-4 | REAR SALES | 1680 | 2963 | 1428 | 2963 | 252 | 0 | 15% | 0%
EF-1 | RESTROOMS | [12 empty] | 400
TOTALS |  | 15330 | 13201 | 13663 | 11335 | 1667 | 1866 |  |  | 0 | 0 | 0 | 0 | 400 | 0
[16 empty] | TRUE | FALSE | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1 | TRUE | FALSE | FALSE
TOTAL OA |  | 1667 | 1866 |  | FRONT
TOTAL EXHAUST |  | 400 | 0 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1 | TRUE
NET AIRFLOW |  | 1267 | 1866 |  | REAR
[5 empty] | AVERAGE | [5 empty] | DESIGN PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1 | 0
[11 empty] | ACTUAL PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 0
NOTES:
DESIGN NET PRESSURIZATION CALCULATION
316.8%