## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | 17240 WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2023-03-23 | Store#: | 17240 | Address: | 305 HIGHWAY 64 WEST LEXINGTON NC 27295
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | NE Front Sales / Entry / Office / Photo | 2003 | FY25 ERF Received | Carrier | 48HJD014—561HY | 1203G30563 | Carrier 12.5 Ton G/E, RTU - DCV, Economizer, Curb Adapter TBD and Furnished by Carrier. Fair condition, no issues observed |  | 12.5 | Gas | 224000 | Unit | Return | RTU | 208 | 208 | 3 | No | 81x53 | 87x58
RTU 2 | SW W Rear Sales / Pharmacy / Breakroom | 2003 | FY25 ERF Received | Carrier | 48HJD014—561HY | 1203G30564 | Carrier 10 Ton G/E, RTU - DCV, Economizer, Curb Adapter TBD and Furnished by Carrier. Fair condition, no issues observed |  | 12.5 | Gas | 224000 | Unit | Return | RTU | 208 | 208 | 3 | No | 81x53 | 87x58
RTU 3 | SE General Sales / Stockroom | 2003 | FY25 ERF Received | Carrier | 48HJD012—571HY | 2103G20491 | Carrier 10 Ton G/E, RTU - DCV, Economizer, Curb Adapter TBD and Furnished by Carrier. Fair condition, no issues observed |  | 10 | Gas | 180000 | Unit | Return | RTU | 208 | 208 | 3 | No | 81x53 | 87x58
RTU 4 | E Rear Sales | 2003 | FY25 ERF Received | Carrier | 50HJ-005—541HY | 2303G20246 | Carrier 5 Ton E/E, RTU - 6.8 KW Electric heat, DCV, Economizer, Curb Adapter TBD and Furnished by Carrier. Fair condition, no issues observed |  | 4 | Electric | 6.8 KW | Unit | Return | RTU | 208 | 208 | 3 | No | 69x41 | 74x45
RTU 5
RTU 6
RTU 7
EH
SPLIT SYSTEM DATA
CU 1 | [6 empty] | *include line set sizes*
CU 2 | [6 empty] | *include line set sizes*
CU 3 | [6 empty] | *include line set sizes*
AHU 1
AHU 2
AHU 3
VENTILATION DATA
ERV 1
ERV 2
EF 1 | Restrooms | N/L | Roof Mounted | Loren Cook | 90C15DH | N/L | Replace at 400 CFM Speed Control - Fair condition, no issues observed |  | N/A | N/A | N/A | N/A | N/A | N/A | 115 | No Safe Access | 1 | No | 16.5x16.5 | 18x18
EF 2
EF 3
EF 4
EF 5
EF 6
EF 7
REFRIGERATION DATA
Roof mounted condenser | Refrigeration | N/L | N/A | Heatcraft | N/L | N/L | Fair condition, no issues observed, data tag sun faded |  | N/A | N/A | N/A | N/A | N/A | N/A | N/L | 208 | N/L | N/A | N/A | N/A
Roof mounted condenser | Refrigeration | N/L | N/A | Heatcraft | N/L | N/L | Fair condition, no issues observed, data tag sun faded |  | N/A | N/A | N/A | N/A | N/A | N/A | N/L | 208 | N/L | N/A | N/A | N/A
Roof mounted condenser
Roof mounted condenser
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | Y | [5 empty] | RTU-1 | Breaker | Square D | FH36100 | 100 | 6 AWG | 1.5"
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) | N |  | Provid partner name: |  |  |  | RTU-2 | Breaker | Square D | KC34125 | 125 | 6 AWG | 1.5"
If Partner Tenant Exists do they have full height walls? (Y/N) | N/A |  | Full height walls are defined as walls up to ceiling.
Obvious "non-typical" Heat Load (Y/N) provide detail in note section | N |  | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | RTU-3 | Breaker | Square D | FH36100 | 100 | 6 AWG | 1.5"
Tenant Space (Y/N): | N |  | Tenant Name (VMD/Kroger/LabCorp, etc.): |  |  |  | RTU-4 | Breaker | Square D | FH36030 | 30 | 10 AWG | 1"
Photo Lab (Y/N): | Y |  | Dry/Wet Lab: Dry
Roof Condition (Good/Fair/Poor): | Fair | [5 empty] | RTU-5
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | Galvanized |  | If "Other" Specify Type: |  |  |  | RTU-6
Unit Hail Damage (Y/N): | N | [5 empty] | RTU-7
Store within 20 Miles of Ocean? (Y/N): | N
Existing EMS (Y/N): | Y |  | EMS Type(FSG/Gridpoint): Griffith Automation Inc.
Fire Alarm Panel Operational (Y/N): | Y |  | Panel Model#: ADT Unimode 10
Photo of Fire Alarm Panel Taken (Y/N): | Y
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | Remote
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: Reach-In
Cooler: Reach-In
Self-Contained Refrigeration ONLY Door Count: | Freezer: N/A
Cooler: N/A
Obvious Visual Damage to MDP (Y/N): | N |  | Explain Visual Damage:
Notes for Installer: | Recommendation: Replace (4) 2003 Carrier RTUs per ERF Received. Replace with Carrier Inventory / Production RTUs as noted on Survey Form. IC to furnish and install 1-3 Stage Cool Thermostats with Sensors for Temperature Control. Replace (1) Roof Exhaust Fan as noted on Survey Form.
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type | Type 4 | Type 4 | Type 4 | Type 4
A (Length) | 87 | 87 | 87 | 74
B (Width) | 58 | 58 | 58 | 45
E | 29.5 Supply | 29.5 Supply | 29.5 Supply | 18.5 Supply
F | 13.5 Return | 13.5 Return | 13.5 Return | 12
G | 40.5 | 40.5 | 40.5 | 33.5
H | 6 | 6 | 6 | 6
I
J
K
L
M
N
O