## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8018 | 6620 | 6199 | 1880 | 1819 | 22.12% | 22.69%
AC-2 | DINNING B / RR | 1280 | 1288 | 830 | 876 | 450 | 412 | 35.16% | 31.99%
AC-3 | DINNING A / DRIVE THRU | 7000 | 6845 | 5175 | 4936 | 1825 | 1909 | 26.07% | 27.89%
AC-4 | PLAY AREA | 1080 | 1043 | 830 | 780 | 250 | 263 | 23.15% | 25.22%
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 | [10 empty] | 1700 | 1707
EF-2 | HD2 | [10 empty] | 701 | 730
EF-3 | HD3 | [10 empty] | 804 | 868
EF-4 | RESTROOM | [12 empty] | 300 | 322
TOTALS |  | 17860 | 17194 | 13455 | 12791 | 4405 | 4403 |  |  | 0 | 0 | 3205 |  | 300
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4405 | 4403 |  | FRONT |  | 0.015 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3505 | 0 |  | SIDE |  | 0.011 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 900 | 4403 |  | REAR |  | 0.013 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.013 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390