## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Kitchen | 2400 | 2373 | 1900 | 1826 | 500 | 547 | 20.83% | 23.05%
RTU-2 | Dining | 3500 | 3583 | 2500 | 2515 | 1000 | 1068 | 28.57% | 29.81%
EF-1 | Cook line | [10 empty] | 2550 | 2580
EF-2 | Bathroom | [12 empty] | 200 | 193
AHU-1 | Back | 400 | 0 | 400
AHU-2 | Back | 400 | 0 | 400
MAU1 | ACPSP | [8 empty] | 1300 | 1178
TOTALS |  | 6700 | 5956 | 5200 | 4341 | 1500 | 1615 |  |  | 1300 | 1178 | 2550 | 2580 | 200 | 193
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2793 |  | FRONT |  | -0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2750 | 2773 |  | SIDE |  | -0.0031 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 20 |  | REAR |  | 0.0078 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00023333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0