## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1(10T) | DINING | 3500 | 1148 | 3200 | 794 | 300 | 354 | 8.571% | 30.84%
RTU-2(10T) | DINING 2 | 3500 | 3770 | 2675 | 2895 | 825 | 875 | 23.57% | 23.21%
RTU-3 | KITCHEN | 1750 | 1495 | 1335 | 1098 | 415 | 397 | 23.71% | 26.56%
RTU-4 | KITCHEN 2 | 3500 | 3263 | 2675 | 3263 | 825 | 0 | 23.57% | 0%
EF-1 | [12 empty] | 399
EF-2 | [12 empty] | 366
EF-3 | [12 empty] | 2146
TOTALS |  | 12250 | 9676 | 9885 | 8050 | 2365 | 1626 |  |  | 0 | 0 | 0 | 2911 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2365 | 1626 |  | FRONT |  | 0.0053 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 0 | 2911 |  | SIDE |  | 0.0105 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 2365 | -1285 |  | REAR |  | 0.0089 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0082333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0