## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 1320 | 1309 | 1145 | 1127 | 175 | 182 | 13.26% | 13.9%
RTU-2 |  | 2580 | 2454 | 2255 | 2140 | 325 | 314 | 12.6% | 12.8%
RTU-3 |  | 4500 | 4508 | 3300 | 3331 | 1200 | 1177 | 26.67% | 26.11%
RTU-4 |  | 4300 | 3953 | 3100 | 2716 | 1200 | 1237 | 27.91% | 31.29%
RTU-5 |  | 5055 | 5171 | 5055 | 5171 | 0 | 0 | 0% | 0%
RTU-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-7 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-8 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-9 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-10 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-11 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-12 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-13 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-14 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-15 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-16 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
MUA-1
MUA-1
EF-1 | RESTROOM | [12 empty] | 325 | 341
EF-2 | IT CLOSET | [12 empty] | 1000 | 978
EF-3
EF-4
EF-5
EF-6
EF-1
EF-2
EF-3
EF-4
EF-5
EF-6
TOTALS |  | 17755 | 17395 | 14855 | 14485 | 2900 | 2910 |  |  | 0 | 0 | 0 | 0 | 1325 | 1319
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2900 | 2910 |  | FRONT |  | 0.019 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1325 | 1319 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1575 | 1591 |  | REAR |  | 0.021 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.02 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0