## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2630 | 2479 | 0 | 100 | 2630 | 2379 | 100% | 95.97%
RTU-2 | DINING | 4000 | 3788 | 2800 | 2601 | 1200 | 1187 | 30% | 31.34%
AC-1 | OFFICE |  |  |  |  | 40 | NA | #DIV/0! | #VALUE!
KEF-1 | HOODS 1/2 | [10 empty] | 2727 | 2756
TX-1 | RESTROOM | [12 empty] | 350 | 363
TOTALS |  | 6630 | 6267 | 2800 | 2701 | 3870 | 3566 |  |  | 0 | 0 | 2727 | 2756 | 350 | 363
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3870 | 3566 |  | FRONT | [10 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3077 | 3119 |  | SIDE |  | 0.017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 793 | 447 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.017 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2670 | #VALUE!
TOTAL KITCHEN EXHAUST |  | 2727 | 2756
NET AIRFLOW |  | -57 | #VALUE!
FCU is brining in OA and dampers are functioning as intended. However there is no access to confirm the exact airflow. Hood is not able to be turned on for building pressure. Side door propped open by welding cables so I measured pressure there.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0