## SPHP-A100
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A100
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1299
Serial Num | 234012165L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1134
Num OA Filters | 2 | OA CFM | 150 | 165
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.8
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A101
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A1011
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1265
Serial Num | 234012142L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1120
Num OA Filters | 2 | OA CFM | 150 | 145
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.7
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A102
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A102
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1290
Serial Num | 234012169L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1123
Num OA Filters | 2 | OA CFM | 150 | 167
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.9
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A103
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A103
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1331
Serial Num | WHC036H4REB | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1164
Num OA Filters | 2 | OA CFM | 150 | 167
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.8
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A104
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A104
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1324
Serial Num | 234012183L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1181
Num OA Filters | 2 | OA CFM | 150 | 143
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.9
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A105
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A105
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1295
Serial Num | 234012195L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1135
Num OA Filters | 2 | OA CFM | 150 | 160
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.9
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A106
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A106
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1330
Serial Num | 234012199L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1155
Num OA Filters | 2 | OA CFM | 150 | 175
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.88
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A107
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A107
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1294
Serial Num | 234012154L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1129
Num OA Filters | 2 | OA CFM | 150 | 165
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.81
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A108
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A108
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1270
Serial Num | 234012179L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1153
Num OA Filters | 2 | OA CFM | 150 | 117
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.88
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A109
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A109
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1310
Serial Num | 234012148L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1155
Num OA Filters | 2 | OA CFM | 150 | 156
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 467/477/481
|  | RL AMPERAGE | 4.3 | 1.8
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A110
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A110
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1361
Serial Num | 234012160L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1184
Num OA Filters | 2 | OA CFM | 150 | 177
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.9
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A111
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A111
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1345
Serial Num | 234012171L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1164
Num OA Filters | 2 | OA CFM | 150 | 181
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.9
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A112
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A112
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1304
Serial Num | 234012175L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1143
Num OA Filters | 2 | OA CFM | 150 | 161
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.87
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-A113
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-A113
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC036H4REB | SF CFM | 1280 | 1332
Serial Num | 234012187L | SF RPM | 996 | HIGH
Configuration | HORIZONTAL | RA CFM | 1130 | 1176
Num OA Filters | 2 | OA CFM | 150 | 156
OA Filter Size | 20X35X2 | RL VOLTAGE | 460 | 460
|  | RL AMPERAGE | 4.3 | 1.85
OA Damper Position
|  | Brake Horsepower | 0.6
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 48 | Fan Suction SP
Horsepower | 0.75 | Fan Discharge SP
Motor RPM | 60HZ | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 4.3 | Total ESP | 1
Service Factor | 1.42

## SPHP-D1091
National TAB
Project: RHSD3 - Lesslie Elem School (Rock Hill, SC)
Asset: SPHP-D1091
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | WHC102 | SF CFM | 3000
Serial Num |  | SF RPM | 1345
Configuration | VERTICAL | RA CFM | 2400
Num OA Filters | 4 | OA CFM | 600
OA Filter Size | 20X25X2 | RL VOLTAGE | 460
|  | RL AMPERAGE | 3.6
OA Damper Position
|  | Brake Horsepower | 1.52
Motor Data |  | Performance Data
Motor MFG |  |  | Design | Actual
Frame |  | Fan Suction SP
Horsepower | 2.75 | Fan Discharge SP
Motor RPM |  | Fan Total SP
Phase | 3 | Coil PD
Rated Voltage | 460 | Pre Filter PD
Rated Amperage | 3.6 | Total ESP | 1
Service Factor