## Report Sheet
STORE #: | 4271 | [7 empty] | 1740 | [14 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | ZAINESVILLE, OHIO | [7 empty] | 1175@60hz | [14 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-19 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | TYLER YOUELLS, MOHAMMED OUARD | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | 580JP12K224A3H0ADA | 4721P91426 | RTU-1 | KITCHEN | 500 | 886 | 0 | 0 |  | 1720 | 1720 | 1059 | 1059 | 4.9 | 211 | 211 | 3 | 14 | 9.4 | 10.1 | 3.3155 | 3.5624 | 7.447%
YORK | 580JP12D224A2A0ADA | 3522P37240 | RTU-2 | DINING | 1000 | 1148 | 1000 | 1016 |  | 1729 | 1729 | 862 | 862 | 3.7 | 210.3 | 210.3 | 3 | 9.2 | 7.46 | 7.47 | 2.6225 | 2.626 | 0.134%
CAPTIVE AIRE | A1-D.250-15 | 5367187 | MUA-1 | HOOD 1 | 1950 | 2056 | 1700 | 1658 | No | 2042 | 1578 | 2042 | 1578 | 2 | 162 | 99 | 3 | 5.48 | 5.3 | 3.9 | 1.4353 | 0.64542 | -55.03%
CAPTIVE AIRE | DU240HFA | 5367187 | EF-1 | HOOD 1 | 3200 | 2867 | 2450 | 2479 | No | 801 | 664 | 801 | 664 | 3 | 122 | 84 | 3 | 9.2 | 6.2 | 5.1 | 1.2644 | 0.71613 | -43.36%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 4090 | 2700 | 2674 |  | FRONT DOOR |  | 0.0013 |  |  | INITIAL | 8.6377 | 4090
|  |  | TOTAL EXHAUST |  | 3350 | 3017 | 2600 | 2629 |  | BACK DOOR |  | 0.004 |  |  | FINAL | 7.55 | 5153
|  |  | NET AIRFLOW |  | 100 | 1073 | 100 | 45 |  | AVERAGE |  | 0.00265 |  |  | ∆ | 1.0877 | -1063
Issue List
Unit # | Description
None

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.