## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 9146 | 7000 | 7398 | 1750 | 1748 | 20% | 19.11%
AC-2 | DRIVE THRU | 5250 | 5402 | 4095 | 4196 | 1155 | 1206 | 22% | 22.33%
AC-3 | DINNING | 5250 | 5191 | 3900 | 3895 | 1350 | 1296 | 25.71% | 24.97%
AC-4 | BOH | 1875 | 1868 | 1375 | 1328 | 500 | 540 | 26.67% | 28.91%
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1832
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1460
EF-3 | RESTROOM | [12 empty] | 300 | 294
TOTALS |  | 21125 | 21607 | 16370 | 16817 | 4755 | 4790 |  |  | 0 | 0 | 3315 | 3292 | 300 | 294
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4755 | 4790 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3586 |  | SIDE |  | 0.003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1140 | 1204 |  | REAR |  | 0.005 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0033333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
BUILDING PRESSURE INITIALLY 0.04" AFTER BALANCING ALL OA FLOWS. WINDY/RAINY CONDITIONS MAY HAVE AFFECTED READINGS. REDUCED AC-2 AND 3 OA FROM 33% TO 30%.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390