## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  |  | 5371 | 0 | 3895 |  | 1476 | #DIV/0! | 27.48%
RTU-2 |  |  | 4807 | 0 | 3559 |  | 1248 | #DIV/0! | 25.96%
PRV 2 | [11 empty] | 1500 | 1506
PRV 3 | [11 empty] | 1500 | 2383
PRV 1 | [13 empty] | 300 | 0
EFA 1 | [13 empty] | 75 | 0
TOTALS |  | 0 | 10178 | 0 | 7454 | 0 | 2724 |  |  | 0 | 0 | 3000 | 3889 | 375 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 0 | 2724 |  | FRONT |  | -0.015 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3375 | 3889 |  | SIDE |  | -0.015 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -3375 | -1165 |  | REAR |  | -0.016 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.015333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0