## Sheet1
Summary
What was found initially: | Manager states that building is hot during the afternoon and and evenings and cold during the day. Humidity causes water droplets on diffusers in the bar area and along side the windowed area of the building. Kitchen was warm in the morning at start up.
Changes made: | RTU's outside airs were adjusted to increase building pressure. EF-3 was turned down to reach target, RTU-2 parameter 154 was sent to "1" for constant airflow.
Air balancing & performance related issues that need to be resolved: | Humidity sensors on RTU 1 and RTU 3 are not wired on unit and RTU 2 does not have the correct wiring for humidity senor on unit(Shielded Twisted Pair). Restroom exhuast is not functional. EF-2 and EF-4 will need pulley changes in order to slow fans down. EF-1 Grill is not completely sealed to the curb causing grease to leak and build up onto roof. RTU-5 is missing it OA filter. RTU-4 OA damper motor is not functional. MUA 1 and MUA 2 will need plulley changes in order to decrease airflow. Hood filters needed to be cleaned or replaced.
Air Balance Schedule
AIR GOING IN (+) | Target | Initial | Final
RTU-1 OA | 750 | 828 | 750
RTU-2 OA | 1500 | 3555 | 1538 |  |  |  | Air Going In |  | Air Going out
RTU-3 OA | 750 | 473 | 754 |  |  |  | 10160 |  | 9561
RTU-4 OA | 750 | 955 | 743
RTU-5 OA | 1000 | 820 | 965
RTU-6 OA | 0
MUA-1 | 2500 | 3910 | 3910
MUA-2 | 1000 | 1500 | 1500
MUA-3 | 0
AIR GOING OUT (-)
EF-1 | 1125 | 2021 | 2021
EF-2 | 1500 | 2959 | 2959 |  |  |  |  | Air Going In - Air Going out =
EF-3 | 2500 | 3226 | 2296 |  |  |  |  | 599
EF-4 | 1050 | 1557 | 1557
EF-5 | 0 | 0 | 0 |  |  |  |  | Building Pressure Average:
EF-6 | 780 | 668 | 728 |  |  |  |  | 0.005
EF-7 | 0 |  | 0
RR Exhaust (Total) | 450 | 0 | 0
NET AIRFLOW (TARGET +200 CFM)
| 845 | 1610 | 599
Target Airflow Calculations
Unit | Tonnage | Target OA | OA %
RTU-1 | 7.5 | 750 | 25%
RTU-2 | 15 | 1500 | 25%
RTU-3 | 7.5 | 750 | 25%
RTU-4 | 7.5 | 750 | 25%
RTU-5 | 10 | 1000 | 25%
RTU-6 |  | 0 | N/A
Hoods | Served by | Served by | Type | Length (in) | Width (in) | MUA Type | Equipment 1 | Equipment 2 | Equipment 3 | CFM/ft1 | CFM/ft 2 | CFM/ft3 | CFM/ft Target | Target Exhaust | Target MUA
Hood 1 | EF-1 | MUA-1 | Type I | 60 | 51 | PSP | Griddle - Flat Top |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1125 | 765
Hood 2 | EF-2 | MUA-1 | Type I | 120 | 51 | PSP | Ovens | Ovens |  | 150 | 150 | NOT FOUND | 150 | 1500 | 1020
Hood 3 | EF-3 | MUA-2 | Type I | 96 | 51 | PSP | Fryers |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 2500 | 1000
Hood 4 | EF-4 | MUA-1 | Type I | 84 | 51 | PSP | Ovens | Ovens |  | 150 | 150 | NOT FOUND | 150 | 1050 | 714
Hood 5 | [9 empty] | NOT FOUND | NOT FOUND | NOT FOUND | 0 | 0 | 0
Restrooms | # of Toilets/Urinals | Target CFM
RR Exhaust (Total) | 6 | 450

## Kitchen Equipment
Equipment | CFM/ft
Char Grill | 275
Fryers | 225
Griddle - Flat Top | 225
Ovens | 150
Salamander | 275
Range | 200

## MUA Type
PSP | 0.8
Short Cycle | 0.5
Back Return | 0.5

## Sheet2
EF-1 | MUA-1 | Type I
EF-2 | MUA-2
EF-3 | MUA-3
EF-4
EF-5
EF-6
EF-7