## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2024-08-07 | Store#: | 17587 | Address: | 6838 Loch Raven Blvd | Towson | MD | 21286
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | RTU/ROOF |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | IF NEAREST EDGE OF RTU IS <10' FROM THE EDGE OF THE ROOF PROVIDE DISTANCE BETWEEN THE TWO EDGES (in) | DOES ROOF HAVE A PARAPET? (Y/N) | DOES RTU/HVAC EQUIPMENT UTALIZE OSHA ROOFTOP GUARD RAILS? (Y/N) | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | Front/Sales | 2012 |  | York | DH120NN20P2AAC1A | NLKM120096 | No Hail guard isntalled. Condenser coil is about 20% deteriorated. Dirty unit filter. Insulatin falling apart in the mixed air comparrtment. |  | 10 | Natural Gas | 240000 BTU | Duct | Return | No | 208 | 193 | 3 | No | No | No | No | 80"X50 | 88"X58"
RTU 2 | Sales | 2012 |  | York | DH120N20P2AAC1A | NLKM120097 | Condenser coil has 30 % of deterioration. |  | 10 | Natural Gas | 240000 BTU | Duct | Return | Yes | 208 | 194 | 3 | No | No | No | No | 80"X50" | 88"X58"
RTU 3 | Pharmacy | 2018 |  | York | ZE060H12B2A1BAA1A | N1D8694138 | No Hail guard installed. Evaporstor coils are slightly dirty. |  | 5 | Natural Gas | 125000 BTU | Duct | Return | Yes | 208 | 193 | 3 | No | No | No | No | 72"X37" | 82"X44"
RTU 4
RTU 5
RTU 6
RTU 7
EH
SPLIT SYSTEM DATA
CU 1 | [6 empty] | *include line set sizes*
CU 2 | [6 empty] | *include line set sizes*
CU 3 | [6 empty] | *include line set sizes*
AHU 1
AHU 2
AHU 3
EVAPORATIVE COOLER/SWAMP COOLER
VENTILATION DATA
ERV 1
ERV 2
STOCK ROOM SF
STOCK ROOM EF
EF 1 | Mens RR | Not Listed | Ceiling | Not Listed | Not Listed | Not Listed | Fan is dirty
EF 2 | Womens RR | Not Listed | Ceiling | Not Listed | Not Listed | Not Listed | Fan is dirty
EF 3
EF 4
EF 5
EF 6
EF 7
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | No | [5 empty] | RTU-1 | Fuse | GE | Not Listed | 60 A | 3/8" | 1-1/4"
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) |  | None |  |  |  |  | RTU-2 | Fuse | GE | Not Listed | 60 A | 3/8" | 1-1/4"
If Partner Tenant Exists do they have full height walls? (Y/N) |  | No |  |  |  |  | RTU-3 | Fuse | GE | Not Listed | 60 A |  | 1"
Obvious "non-typical" Heat Load (Y/N) provide detail in note section |  | No |  |  |  |  | RTU-4
Tenant Space (Y/N): | No
Photo Lab (Y/N): | Yes |  | Dry Lab |  |  |  | RTU-5
Roof Condition (Good/Fair/Poor): | Good | [5 empty] | RTU-6
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | Galvanized | [5 empty] | RTU-7
Unit Hail Damage (Y/N): | No | [5 empty] | CU 1
Store within 20 Miles of Ocean? (Y/N): | No | [5 empty] | CU 2
Existing EMS (Y/N): | No |  | EMS Type(FSG/Gridpoint): |  |  |  | CU 3
Fire Alarm Panel Operational (Y/N): | Could not locate fire alarm panel |  | Panel Model#: |  |  |  | AHU 1
Photo of Fire Alarm Panel Taken (Y/N): |  | No |  |  |  |  | AHU 2
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | Remote Condensing Unit | [5 empty] | AHU 3
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: |  | Reach In |  |  |  | EVAPORATIVE COOLER/SWAMP COOLER
| Cooler: |  | Reach In |  |  |  | STOCK ROOM SF
Self-Contained Refrigeration ONLY Door Count: | Freezer: | [5 empty] | STOCK ROOM EF
Cooler:
Obvious Visual Damage to MDP (Y/N): | No |  | Explain Visual Damage:
Notes for Installer:
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type | 1 | 1 | 1
A (Length) | 50" | 50" | 37"
B (Width) | 80" | 80" | 72"
E | 28" | 28" | 18"
F | 16" | 16" | 11"
G | 16" | 16" | 18"
H | 26" | 26" | 18"
I | 7" | 7" | 6"
J | 10" | 10" | 9"
K | 16" | 16" | 5"
L | 36" | 36" | 36"
M | 7" | 7" | 6"
N
O
RETURN
SUPPLY