## SUMMARY (2)
INITIAL AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 2974 | 2720 | 2645 | 680 | 329 | 20% | 11.06%
RTU-2 | KITCHEN | 5200 | 4740 | 4160 | 4068 | 1040 | 672 | 20% | 14.18%
RTU-3 | KITCHEN | 5200 | 4670 | 4160 | 4080 | 1040 | 590 | 20% | 12.63%
RTU-4 | KITCHEN | 10000 | 9196 | 8000 | 8219 | 2000 | 977 | 20% | 10.62%
RTU-5 | HOST AREA | 1600 | 1391 | 1280 | 1391 | 320 | 0 | 20% | 0%
RTU-6 | MAIN DINING | 1200 | 1163 | 960 | 1163 | 240 | 0 | 20% | 0%
RTU-7 | MAIN DINING | 4000 | 3893 | 3200 | 3355 | 800 | 538 | 20% | 13.82%
RTU-8 | PRIVATE DINING | 1200 | 0 | 960 | 0 | 240 | 0 | 20% | 0%
RTU-9 | PRIVATE DINING | 2000 | 1867 | 1600 | 1867 | 400 | 0 | 20% | 0%
RTU-10 | MAIN DINING | 1200 | 879 | 960 | 879 | 240 | 0 | 20% | 0%
DOAS-1 | UNKNOWN | NA | 0 | NA | 0 | NA | 0 | 100% | 0%
DOAS-2 | UNKNOWN | NA | 0 | NA | 0 | NA | 0 | 100% | 0%
EF-1 | HOOD-4 | [10 empty] | 3200 | 3094
EF-2 | HOOD-3 | [10 empty] | 2345 | 2059
EF-3 | HOOD-2 | [10 empty] | 3000 | 2805
EF-4 | HOOD-5 | [10 empty] | 1275 | 1060
EF-5 | RESTROOM | [12 empty] | 300 | 319
MUA-1 | HOODS | [8 empty] | NL | 2158
MUA-2 | HOODS | [8 empty] | NL | 912
TOTALS |  | 35000 | 30773 | 28000 | 27667 | 7000 | 3106 |  |  | NL | 3070 | 9820 | 9018 | 300 | 319
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | NA | 6176 |  | FRONT |  | -0.017 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | NA | 9337 |  | SIDE |  | -0.015 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | NA | -3161 |  | REAR |  | -0.013 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.015 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
NO DESIGN AIR FLOW GIVEN FOR ANY EQUIPMENT. RTU SUPPLY BASED ON 400 CFM/TON. RTU OA 20% OF SUPPLY. EF DESIGN BASED ON TYPICAL CFM/FOOT OF HOOD BASED ON KITCHE EQUIPMENT
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0