## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 4311 | 4100 | 3660 | 900 | 651 | 18% | 15.1%
DOAS-1 | KITCHEN | 2900 | 2599 | 0 | 0 | 2900 | 2599 | 100% | 100%
KEF-1 | HOOD 1 | [10 empty] | 1600 | 1547
KEF-2 | HOOD 2 | [10 empty] | 775 | 812
KEF-3 | HOOD 3 | [10 empty] | 525 | 568
EF-1 | MENS RR | [12 empty] | 225 | 209
EF-2 | WOMENS RR | [12 empty] | 75 | 68
EF-3 | WOMENS RR | [12 empty] | 75 | 78
TOTALS |  | 7900 | 6910 | 4100 | 3660 | 3800 | 3250 |  |  | 0 | 0 | 2900 | 2927 | 375 | 355
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3800 | 3250 |  | FRONT |  | 0.049 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3275 | 3282 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 525 | -32 |  | REAR |  | 0.0074 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.0282 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
OA and building pressure taken under very windy conditions and may not be accurate.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0