## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 4200 | 3656 | 3350 | 2842 | 850 | 814 | 20.24% | 22.26%
RTU-2 | SALES | 4200 | 3619 | 3200 | 2567 | 1000 | 1052 | 23.81% | 29.07%
RTU-3 | PHARMACY | 2730 | 2963 | 2730 | 2963 | 0 | 0 | 0% | 0%
EF-1 | MENS RR | [13 empty] | 74
EF-2 | WOMENS RR | [13 empty] | 56
EF-3 | [14 empty] | 113
TOTALS |  | 11130 | 10238 | 9280 | 8372 | 1850 | 1866 |  |  | 0 | 0 | 0 | 0 | 0 | 243
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1850 | 1866 |  | FRONT | [10 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 0 | 243 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1850 | 1623 |  | REAR | [10 empty] | 0
[5 empty] | AVERAGE | [5 empty] | DESIGN PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 0
TRUE
[11 empty] | ACTUAL PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1
NOTES:
DESIGN NET PRESSURIZATION CALCULATION
#DIV/0!